## Assumptions
Solar + Battery + Grid Compute Site — assumptions (edit yellow)
A 4MW grid IMPORT connection guarantees 24/7/365 power (so ~90% GPU utilisation — fixes the seasonal mismatch). Solar + LFP battery cut the power COST, not the utilisation.
SITE
Grid IMPORT connection (MW) | 4
Compute load (MW) | 4
Solar array (MWp) | 8
LFP battery usable (MWh, 1 cycle/day) | 8
Utilisation (grid-backed) | 90%
Daylight window (h, when solar offsets load) | 12
POWER PRICES (p/kWh)
Solar LCOE (your panels' £/kWh) | 4 | UK ground-mount solar ~£30–50/MWh
Grid NIGHT / off-peak | 13 | Economy-7 / wholesale night ~10–14p
Grid DAY / peak | 25
Battery amortisation per kWh cycled | 4.6 | LFP £250/kWh ÷ 6,000 cycles ÷ 0.9 ≈ 4.6p
Battery round-trip efficiency | 90%
COMPUTE (the 3-year consumable)
Compute capex £/MW (chips+servers+heat) | 5630000
Revenue £/MWh of power drawn (contracted) | 560 | £560/MWh = contracted £0.25/hr per 0.45kW GPU. SPOT is far lower — see note.
Maintenance (% capex/yr) | 5%
Other opex £/MW/yr | 30000
Chip ECONOMIC life (yrs) — payback MUST beat this | 3 | V100 (8yr) now rents $0.02/hr — chips die economically at ~3 yr
ENERGY INFRASTRUCTURE (the 25-year durable asset)
Solar capex £/MWp | 600000
LFP battery capex £/MWh | 250000
Grid connection capex £ | 1000000

## Monthly Energy
UK year, month by month — where the power comes from (all MWh)
Solar serves daytime load first; surplus charges the battery; battery covers evening; grid (cheap night / peak day) backstops. Live off Assumptions.
Month | Days | PSH | Solar gen | Day load | Night load | Solar→day | Surplus | →Battery | Curtailed | Batt→night | Grid day | Grid night | Cost £
Jan | 31 | 0.74
Feb | 28 | 1.36
Mar | 31 | 2.31
Apr | 30 | 3.42
May | 31 | 4.38
Jun | 30 | 4.5
Jul | 31 | 4.35
Aug | 31 | 3.78
Sep | 30 | 2.82
Oct | 31 | 1.61
Nov | 30 | 0.86
Dec | 31 | 0.6
TOTAL
Blended power cost (p/kWh)
Solar self-consumed (%)
Curtailed solar (% of gen) — wasted

## Economics
Economics — two assets: 3-yr chips on 25-yr energy infrastructure
POWER (from the monthly sim)
Power drawn (MWh/yr)
Blended power cost (p/kWh) | vs 25p naive grid / ~19p smart all-grid
Annual power bill £
COMPUTE LAYER (3-yr chips)
Compute capex £ (load × £/MW)
Revenue £/yr (contracted)
− Power bill
− Maintenance
− Other opex
NET £/yr
Compute PAYBACK (months)
Chip economic life (months)
Verdict vs chip life
ENERGY INFRASTRUCTURE LAYER (25-yr durable asset)
Solar capex £
Battery capex £
Grid connection capex £
Energy infra capex £ (total)
Power saving vs 19p smart-grid £/yr
Energy infra payback (yrs) — 25-yr life
WHOLE SITE
Total capex £ (compute + energy)
Net £/yr (after power, before energy-infra amort)
THE CATCH: revenue assumes you have SOLD all this compute at contracted rates (~90% util). You do NOT have that demand yet — it is the single biggest assumption. At SPOT/typical rates (~55% util, lower £/MWh) the revenue roughly HALVES and payback blows past chip life.

## Solar Sweep
How much solar to pair with the 4MW connection? (battery 8MWh, 90% util)
More solar → cheaper power, but past ~2× the load you curtail (waste) summer surplus without a bigger battery or export. Static snapshot; the live model is on 'Monthly Energy'.
Solar (MWp) | Blended p/kWh | Curtailed % | Save vs 25p grid £/yr | Save vs 19p grid £/yr | Solar:load ratio
0 | 19 | 0% | 1892160 | 0 | 0.0×
4 | 16.5 | 0% | 2679198 | 787038 | 1.0×
8 | 14 | 0% | 3466236 | 1574076 | 2.0×
12 | 12.1 | 1.398% | 4080234 | 2188074 | 3.0×
16 | 11.2 | 14.49% | 4360479 | 2468319 | 4.0×
20 | 10.6 | 25.78% | 4541383 | 2649223 | 5.0×
SWEET SPOT: ~6–10 MWp (1.5–2.5× the load) self-consumes nearly all generation with a modest battery. Beyond that you need either a much bigger (expensive) battery or an export connection to avoid wasting summer sun.
KEY INSIGHT: if you already have CHEAP NIGHT GRID (~13p), a big battery is hard to justify — the grid is a cheaper 'battery' than a battery. The physical battery earns its keep mainly by capturing summer solar surplus and shaving peak-day grid. Size it small.

## Notes & Sources
Notes & Sources
CHIP LIFE — the binding constraint
GPU rental rate collapses ~80–95% over 5–6 yrs | V100 (2017) now $0.02/hr; 2080 Ti (2018) $0.11/hr — economic life ~3 yr
→ compute must pay back inside ~3 yr | Energy infra (solar/battery/grid) is the 25-yr durable asset; chips are a rolling 3-yr consumable
BATTERY — which and why
LFP (lithium iron phosphate) is the right chemistry | Cheapest, safest, ~6,000-cycle life for daily solar-shift. £200–350/kWh installed (UK 2026)
Size it SMALL with a grid connection | Cheap night grid (~13p) is a cheaper 'store' than a battery (~9p delivered BUT huge capex). Battery's job: capture summer surplus + shave peak day
SOLAR
UK ground-mount LCOE ~£30–50/MWh (3–5p) | ~937 kWh/kWp/yr; 10–11% capacity factor; summer ~8× winter output
Pair ~1.5–2.5× the load | Beyond that, curtailment without bigger battery or export
THE MODEL'S LOAD-BEARING ASSUMPTION
Revenue assumes CONTRACTED demand at ~90% util | You do NOT have this. Spot/typical demand ≈ half the revenue and breaks the payback. This is the bet, not the power.
Grid IMPORT connection is the unlock | A small import connection (for winter/nights) is far easier to get than a big EXPORT connection — that is the real edge for queue-blocked solar
SOURCES
UK solar irradiance / PSH by month | https://re.jrc.ec.europa.eu/pvg_tools/en/
UK grid connection queue / curtailment | https://www.nationalgrideso.com/industry-information/connections
LFP grid battery costs 2026 | https://www.nrel.gov/analysis/tech-cost-analysis.html
Vast.ai per-GPU rates (V100/2080Ti collapse) | https://vast.ai/pricing/gpu/TESLA-V100