## Executive Summary
ForgeOS Engineering Dossier — Water treatment
⬤ TAB QUALITY 9/10 · PASS (target ≥8, live from the Quality & Audit score cell) · MIRROR of the dossier floor (min of every deterministic section & non-mirror tab) — re-stamped from the CURRENT scores, never a stale earlier cap; own content check: cov… · full audit: Quality & Audit tab
The engineering reality of your hardware idea — a buildable design, a real bill of materials, the true cost, and who can make it. The detail is in the tabs; this page is the summary.
WHAT IT IS
Water treatment
OUTPUT
45 m3/h
Irrigation Demand M3 Per
ALL-IN INSTALLED COST
£1,360,613
STATUS
SHIPS
One verdict for the whole dossier — the floor is the minimum score of every section and tab; it ships when all are ≥8. Detail: Quality & Audit tab.
SG: The original Codema quote was for 2 x 90m3 and 1 x 45m3 system with RO etc for 1.1m Euros.
This dossier specifies a Water treatment — 45 m3/h (irrigation demand m3 per). The engine values the build at £1,360,613 (all-in installed cost). An independent market benchmark flags 1 dimension where the design diverges from the brief/market expectation — see the ⚠ Checks tab for the routed detail. Every figure in this workbook — the bill of materials, the costs, and the specifications below — is derived deterministically from the engineering contract, computed rather than estimated by hand. | [8 empty] | SG: Does the model take into account inflation each year and material price index rises etc?
Key specifications & brief compliance — every target deterministically verified
Brief metric | Target | Unit | Matched contract quantity | Achieved | Direction | STATUS | Note | Cell check
Irrigation demand (m³/h) | 45 | m3/h | Irrigation pump flow (m³/h) | 90 | ≥ target (meet/exceed) | PASS | brief key: irrigation_demand_m3_per_hr → contract: irrigation_pump_flow_m3_h · unit family: flow_m3h | PASS | SG: Why is it providing double capacity required? May be a good thing for resilience of the system etc maybe.
Cultivation containers | 6000 | count | Cultivation container count | 6000 | ≥ target (meet/exceed) | PASS | brief key: cultivation_containers → contract: cultivation_container_count · unit family: count | PASS | SG: 45m3/hr for 6,000 containers sounds low. Is a 'container' more like a bench tray? Maybe language issue.
Ro permeate capacity (m³/h) | 8 | m3/h | Ro permeate capacity (m³/h) | 8 | ≥ target (meet/exceed) | PASS | brief key: ro_permeate_capacity_m3_per_hr → contract: ro_permeate_capacity_m3_h · unit family: flow_m3h | PASS | SG: RO capacity for 6,000 containers again sounds low.
Ro recovery (%) | 75 | % | Ro recovery (%) | 75 | ≥ target (meet/exceed) | PASS | brief key: ro_recovery_percent → contract: ro_recovery_percent | PASS
Water storage capacity m3 | 120 | m3 | Water storage capacity m3 | 120 | ≥ target (meet/exceed) | PASS | brief key: water_storage_capacity_m3 → contract: water_storage_capacity_m3 · unit family: volume_m3 | PASS
Actuated valves | 200 | count | Actuated distribution valve count | 200 | ≥ target (meet/exceed) | PASS | brief key: actuated_valves → contract: actuated_distribution_valve_count · unit family: count | PASS
Where the money goes — capex by category
Pipework & valves | 339593 |  | 41.6 | █████████████████
Filtration & membranes | 111964 |  | 13.7 | █████
Controls & instrumentation | 110691 |  | 13.6 | █████
Vessels, tanks & columns | 108361 |  | 13.3 | █████
Other equipment | 65562 |  | 8 | ███
Rotating equipment | 35261 |  | 4.3 | ██
Power & electrical | 34221 |  | 4.2 | ██
What's inside this workbook
• Bill of Materials (Ledger) | The bill — tag, item, qty, unit £, cost basis, spec.
• Cost waterfall | Bill of materials to installed price, with live running totals.
• Financial model | Economics, scenarios and investment analysis, live off the Inputs tab.
• Calculations | Worked calculations by tool — live Excel formulas where structured.
• Risk & Regulatory | Hazard and risk register, compliance verdict and statutory duties.
• Connection trace | Which part connects to what, with live cell references.
Your next steps — from design to a funded factory
• You have the engineering dossier
A buildable design, a real bill of materials, and the true cost — this document.
→ Talk to the experts this design needs
We connect you to vetted specialists for the open questions the design raises.
→ Get real supplier quotes (RFQ)
We take this bill of materials to suppliers and bring back real quotes.
→ Raise the money on these numbers
We help you turn the validated design and costs into a fundraise.
Fractional Forge — Tristan Fischer, Founder. Reply to take the next step.

## Contents
Contents
⬤ TAB QUALITY 10/10 · PASS (target ≥8, live from the Quality & Audit score cell) · index integrity (both directions) — index rows point at an existing tab 32/32; every sheet listed in the index 32/32; cell completeness+type contract 96/96 · score = min… · full audit: Quality & Audit tab
Click any tab name to jump to it. Each data tab has a '↑ Contents' link at its top-right to come back. Yellow cells anywhere are editable inputs; green cells are live formulas.
# | Tab | What's on it | Cell check
1 | Executive Summary | The cover — what it is, cost, verdict and next steps. | PASS
2 | Inputs Master (M0) | Every primitive number behind the model, with class and provenance. | PASS
3 | Equipment & Dimensions Register | Every manifest part — geometry, volume formula, MPN, coverage. | PASS
4 | Overview | Run provenance, quality scorecard and headline metrics. | PASS
5 | Renders | Photoreal render gallery — interior hero, plan and exterior views. | PASS
6 | Cost waterfall | Bill of materials to installed price, with live running totals. | PASS
7 | Financial model | Economics, scenarios and investment analysis, live off the Inputs tab. | PASS
8 | Bill of Materials (Ledger) | The bill — tag, item, qty, unit £, cost basis, spec. | PASS
9 | Brief | Original client brief and the engine's structured interpretation. | PASS
10 | Design basis | Codes, design duties, fluid and utilisation basis — with sources. | PASS
11 | Drawings | Drawing register — number, revision, scale, sheets and full-size A1 files. | PASS
12 | BFD — Block Flow | Block flow diagram — major process blocks & streams. | PASS
13 | P&ID | Piping & instrumentation diagram — process flow, valves, instruments. | PASS
14 | Process schedules | Valve and instrument schedules; the line list is Line & velocity. | PASS
15 | GA — General Arrangement | General arrangement — equipment layout & footprint. | PASS
16 | HVAC | Ventilation & climate-control schematic. | PASS
17 | Electrical | Single-line diagram with the panel/load schedule — one dataset. | PASS
18 | Line & velocity | THE line list — every sized run versus its limit. | PASS
19 | Assembly sequence | Order of works from civils through to commissioning. | PASS
20 | Risk & Regulatory | Hazard and risk register, compliance verdict and statutory duties. | PASS
21 | Holds & exclusions | Numbered open holds derived live from failing checks; scope exclusions. | PASS
22 | Questions for the customer | Numbered confirm-or-correct questions — assumptions, gaps and offer divergences. | PASS
23 | Quality & Audit | Sections, per-tab scores and audit findings — one verdict. | PASS
24 | Sense-check | Independent market benchmark versus the engine's numbers. | PASS
25 | ⚠ Checks | Live arithmetic invariants — red rows show numbers that don't reconcile. | PASS
26 | Connection trace | Which part connects to what, with live cell references. | PASS
27 | Quantities | Every sized contract quantity with family, basis and source. | PASS
28 | Calculations | Worked calculations by tool — live Excel formulas where structured. | PASS
29 | Inputs & Assumptions | Editable yellow drivers feeding the economics model. | PASS
30 | Part names | Master parts list; every other tab references these cells. | PASS
31 | Glossary | Plain-English meaning of every abbreviation in the workbook. | PASS
32 | Audit data | Embedded operands every live verdict formula references, with provenance. | PASS

## Inputs Master (M0)
M0 — Inputs Master: every primitive number the model is built from | [6 empty] | ↑ Contents
⬤ TAB QUALITY 10/10 · PASS (target ≥8, live from the Quality & Audit score cell) · cell completeness+type contract 270/270 · score = min over checks of 10 × passed/checked · full audit: Quality & Audit tab
A PRIMITIVE = a number with NO in-model ancestor: brief-stated, a class assumption (open until the customer confirms), a physics constant, a live catalogue/distributor price, or a margin/install/corpus factor. Every row mints an Excel DEFINED NAME (Ref) so a downstream formula can reference it by name and self-document. Phase A: this register exists, fully cited. Phase B rewires the rest of the workbook to reference these cells live.
Ref | Label | Value | Units | Class | Provenance | Used-by count | Cell check
INP_UNIT_COST_CEILING | Unit cost ceiling | 1400000 | GBP | brief | brief: "…per year - Unit cost ceiling: approximately £1,250,000 to £1,400,000 installed for the water, storage, fertigation, irrigation a…" | 0 | PASS | SG: What defines this ceiling?
INP_BATCH_SIZE | Batch size | 6 | count | brief | brief: "…al turnkey supplier offer (Codema Systems Group, offer 3201262, "Farm 2", 2020) totalling €1,395,019. Target market: ind…" | 113 | PASS
INP_DESIGN_LIFE | Design life | 20 | years | brief | brief: "…a real turnkey supplier offer (Codema Systems Group, offer 3201262, "Farm 2", 2020) totalling €1,395,019. Target market:…" | 108 | PASS
INP_IRRIGATION_DEMAND_M3_PER_HR | Irrigation demand m3 per hr | 45 | m3/h | brief | brief: "…R (FERTIGATION) UNITS — two A/B nutrient-dosing units, each 45 cubic metres per hour, for the multi-layer ebb/flow system,…" | 43 | PASS
INP_CULTIVATION_CONTAINERS | Cultivation containers | 6000 | count | brief | brief: "…ayers per tunnel, 4 rows per layer, 15 containers per row — 6,000 cultivation containers total, each 2,760 by 1,290 millimetr…" | 10 | PASS
INP_RO_PERMEATE_CAPACITY_M3_PER_HR | Ro permeate capacity m3 per hr | 8 | m3/h | brief | brief: "…tem needs. - Reverse-osmosis unit: hourly permeate capacity 8.0 cubic metres per hour, raw-tap-water blending capacity 1.2…" | 58 | PASS
INP_RO_RECOVERY_PERCENT | Ro recovery percent | 75 | % | brief | brief: "…capacity 1.2 to 1.6 cubic metres per hour, recovery factor 75 percent, working pressure 10.6 bar at 15 degrees Celsius fe…" | 7 | PASS
INP_WATER_STORAGE_CAPACITY_M3 | Water storage capacity m3 | 120 | m3 | brief | brief.constraints.target_performance.metrics[water_storage_capacity_m3] (source: user) | 4 | PASS
INP_ACTUATED_VALVES | Actuated valves | 200 | count | brief | brief: "…iner at 1.5 cubic metres per hour; 30 containers per valve, 200 electrically-actuated valves; one valve per department open…" | 14 | PASS
INP_SALE_PRICE_PER_OUTPUT_UNIT | Sale price (per output unit) | 0 | £/m3/h | assumption | UNVERIFIED — no per-unit market price is derivable for this class. Enter a real sale price to make the economics tabs meaningful; until then revenue / EBITDA / IRR are not valid. — ASSUMPTION, open until the customer confirms (see 'Questions for the customer') | 147 | PASS
INP_CONSUMABLES_PRICE_DOSING_CHEMICALS_NUTRIENT_FERTILISER_STOCK_FILTER_MEDIA_MEMBRANES | Consumables price (dosing chemicals · nutrient / fertiliser stock · filter media & membranes) | 0 | £/m3/h | assumption | consumable classes derived from the plant's own process/media BoM + contract lines — what it ACTUALLY consumes (not a 'feedstock'); enter a real £ per output unit to price them (0 until priced — meanwhile carried inside 'Other opex') — ASSUMPTION, open until the customer confirms (see 'Questions for the customer') | 147 | PASS
INP_CONSUMABLE_INTENSITY_RATIO | Consumable intensity ratio | 0 | ratio | assumption | consumable units per output unit (multiplies the consumables price above); 0 until priced — ASSUMPTION, open until the customer confirms (see 'Questions for the customer') | 147 | PASS
INP_ENERGY_PRICE | Energy price | 0.15 | £/kWh | assumption | assumed — UK industrial electricity ~£0.15/kWh (edit to your tariff) — ASSUMPTION, open until the customer confirms (see 'Questions for the customer') | 0 | PASS
INP_ELECTRICAL_LOAD_FACTOR | Electrical load factor | 0.65 | avg/peak | assumption | assumed average/peak electrical load factor — supply a class duty-cycle to refine — ASSUMPTION, open until the customer confirms (see 'Questions for the customer') | 0 | PASS
INP_OPERATING_HOURS | Operating hours | 8000 | h/yr | assumption | assumed — typical process-plant annual operating hours (supply a class duty-cycle to refine) — ASSUMPTION, open until the customer confirms (see 'Questions for the customer') | 1 | PASS
INP_WATER_UTILISATION_DELIVERED_DESIGN_FLOW | Water utilisation (delivered ÷ design flow) | 0.25 | fraction | assumption | multiplies the design flow above · assumed — the design flow is the PEAK simultaneous demand, so annual delivered volume = design flow × 8760 h × this factor. 0.25 models an intermittent, demand-driven duty (sequenced valve sections / batch draw-off deliver ≈25% of the peak run continuously); set ≈0.9 for a continuous process duty, or edit to metered annual demand ÷ (design flow × 8760). Drives the levelised £/m³ on the Financial model — the electrical load factor above sizes the ENERGY line only. — ASSUMPTION, open until the customer confirms (see 'Questions for the customer') | 0 | PASS
INP_LABOUR | Labour | 25000 | £/yr | assumption | assumed — supply a real figure. No operating headcount signal, so this is defaulted as an UNMANNED / skid plant: ~£25,000/yr for remote monitoring + periodic maintenance visits (NOT a % of capex). Enter your real annual labour cost, or supply an operating headcount. — ASSUMPTION, open until the customer confirms (see 'Questions for the customer') | 0 | PASS
INP_MAINTENANCE | Maintenance | 3 | % capex/yr | factor | process-plant norm | 128 | PASS
INP_OTHER_OPEX | Other opex | 27212 | £/yr | assumption | assumed — 2% of installed capex/yr (consumables, insurance, overhead; supply a class opex model to refine) — ASSUMPTION, open until the customer confirms (see 'Questions for the customer') | 0 | PASS
INP_SCALING_EXPONENT_N_CAPEX_OUTPUT_N | Scaling exponent n (capex ∝ output^n) | 1 | n | factor | 1.0 = LINEAR — a MODULAR plant scaled by replicating identical units (more tanks/pumps/skids); capex per output unit is constant, de-risked + testable at small scale (the ForgeOS default for modular plant). 0.6 = the six-tenths law for MONOLITHIC equipment that scales by getting bigger. Edit to model either regime — every capex/economics cell on the sweep + solver recomputes live off this. | 134 | PASS
INP_DISCOUNT_RATE | Discount rate | 10 | % | factor | real WACC for a small infrastructure project | 20 | PASS
INP_INVESTOR_HURDLE_RATE_IRR | Investor hurdle rate (IRR) | 15 | % | factor | the minimum IRR an investor demands before deploying capital — the 'investable' bar on the Investment Analysis tab; edit to your fund's threshold | 13 | PASS
INP_PROJECT_LIFE | Project life | 20 | yr | assumption | asset economic life for the NPV horizon — ASSUMPTION, open until the customer confirms (see 'Questions for the customer') | 108 | PASS
INP_PROCESS_FLUID_DENSITY_ENGINE_DEFAULT | Process fluid density (engine default) | 1000 | kg/m3 | constant | engine default — process-fluid density (median of 3 engine worked-calc input(s)) | 0 | PASS
INP_SWEET_SPOT_CAPACITY_SCALING_EXPONENT_N | Sweet-spot capacity-scaling exponent (n) | 0.65 | n (dimensionless) | constant | sweet-spot.ts DEFAULT_N — the six-tenths capacity-scaling-law exponent (chemical-plant cost-scaling literature default, n≈0.6–0.7); a hardcoded engine default, not case-specific to this run | 0 | PASS
INP_WATER_DENSITY_PUMP_SIZING_WORKED_CALC | Water density (pump-sizing worked calc) | 1000 | kg/m3 | constant | irrigation:pump-sizing · "Pump hydraulic power" assumption: "P = rho x g x Q x H, water rho 1000 kg/m3, g 9.81 m/s2" | 0 | PASS
INP_STANDARD_GRAVITATIONAL_ACCELERATION | Standard gravitational acceleration | 9.81 | m/s2 | constant | irrigation:pump-sizing · "Pump hydraulic power" assumption: "P = rho x g x Q x H, water rho 1000 kg/m3, g 9.81 m/s2" | 0 | PASS
INP_ABB_CIRCUIT_BREAKERS | ABB Circuit Breakers | 283 | £ | catalogue | db:farnell · MPN 1SDA067417R1 · 0 in stock | 0 | PASS
INP_WAGO_TERMINAL_BLOCKS | WAGO Terminal Blocks | 1.2 | £ | catalogue | db:farnell · MPN 2002-1301 · 6053 in stock | 7 | PASS
INP_TDK_LAMBDA_3_PHASE_POWER_INPUT | TDK-Lambda 3 Phase Power Input | 168 | £ | catalogue | db:mouser · MPN DRB240-24-3-A0 · 16 In Stock | 0 | PASS
INP_ABB_CIRCUIT_BREAKER | ABB Circuit Breaker | 283 | £ | catalogue | db:lm-only · MPN 1SDA067417R1 | 0 | PASS
INP_PRAHER_BACKWASH_SERVICE_VALVE_NEST | Praher Backwash / Service Valve Nest | 0 | £ | catalogue | db:tavily · MPN AQUASTAR 4000 | 147 | PASS
INP_WEDECO_XYLEM_UV_DISINFECTION | WEDECO (Xylem) Uv Disinfection | 0 | £ | catalogue | db:tavily · MPN Spektron 30e | 147 | PASS
INP_PENTAIR_STRUCTURAL_SOFTENER_VESSEL | Pentair Structural Softener Vessel | 0 | £ | catalogue | db:lm-only · MPN 36X72 COMP 6"TF 6"BF | 147 | PASS
INP_GRUNDFOS_FERTIGATION_DOSING_PUMP | Grundfos Fertigation Dosing Pump | 0 | £ | catalogue | db:tavily · MPN 96122012 | 147 | PASS
INP_INSTALL_FACTOR | Install factor | 0.4 | ratio | factor | costStack.ratios_applied.install_factor — Water / fertigation / irrigation plant — FIELD-ERECTED (built on site, NO factory/margin/channel). Installed CAPEX = raw materials + field installation + FOAK/contingency + EPC/engineering. | 10 | PASS
INP_FOAK_CONTINGENCY_FACTOR | FOAK contingency factor | 0.18 | ratio | factor | costStack.ratios_applied.foak_contingency_factor — Water / fertigation / irrigation plant — FIELD-ERECTED (built on site, NO factory/margin/channel). Installed CAPEX = raw materials + field installation + FOAK/contingency + EPC/engineering. | 0 | PASS
INP_EPC_ENGINEERING_FACTOR | EPC/engineering factor | 0.12 | ratio | factor | costStack.ratios_applied.epc_engineering_factor — Water / fertigation / irrigation plant — FIELD-ERECTED (built on site, NO factory/margin/channel). Installed CAPEX = raw materials + field installation + FOAK/contingency + EPC/engineering. | 0 | PASS
INP_INSTALLED_COST_FACTOR_CENTRAL | Installed-cost factor (central) | 3 | × | factor | costBasis.rollup.install_factor_central — Installed = purchased × skid-modular factor 2.5–3.5 (not the stick-built 4.74). Excludes contingency + EPC + owner's cost; add ~30% for an all-in figure. | 128 | PASS
INP_CORPUS_MEDIAN_UV_DISINFECTION_4_KW_600X510X660_MM | Corpus median — Uv Disinfection · 4 kW · 600x510x660 mm | 34360 | £ | factor | corpus anchor, median £34,360, n=5 · tag V-102 | 1 | PASS
INP_CORPUS_MEDIAN_SOFTENER_VESSEL_1_2_M_DIA_X_1_3_M | Corpus median — Softener Vessel · 1.2 m dia x 1.3 m | 12581 | £ | factor | corpus anchor, median £12,581, n=5 · tag V-106 | 1 | PASS
INP_CORPUS_MEDIAN_GAC_FILTER_1_3_M_DIA_X_1_4_M | Corpus median — Gac Filter · 1.3 m dia x 1.4 m | 18 | £ | factor | corpus anchor, median £18, n=5 · tag V-101 | 10 | PASS
INP_CORPUS_MEDIAN_HOOGENDOORN_ISII_REMOTE_MONITORING | Corpus median — Hoogendoorn iSii Remote Monitoring | 982 | £ | factor | corpus anchor, median £982, n=5 · tag X-118 | 1 | PASS
INP_CORPUS_MEDIAN_LEVEL_TRANSMITTER_0_1_4_M | Corpus median — Level Transmitter · 0–1.4 m | 2800 | £ | factor | corpus anchor, median £2,800, n=5 · tag LT-201–213 | 4 | PASS
INP_CORPUS_MEDIAN_CLEANING_TANK_1_4_M_DIA_X_1_3_M | Corpus median — Cleaning Tank · 1.4 m dia x 1.3 m | 8082 | £ | factor | corpus anchor, median £8,082, n=5 · tag TK-102 | 2 | PASS

## Equipment & Dimensions Register
Equipment & Dimensions Register — one row per manifest part, self-auditing geometry | [14 empty] | ↑ Contents
⬤ TAB QUALITY 9.9/10 · PASS (target ≥8, live from the Quality & Audit score cell) · cell completeness+type contract 417/423 · score = min over checks of 10 × passed/checked · full audit: Quality & Audit tab
VOLUME and FOOTPRINT are IN-CELL FORMULAS over the L/W/H or D/H columns — corrupt a dimension and they move on recalc, never a python-baked number. 'Canonical name' is the ONE name registry for this part; the two check columns cross-reference the BoM ledger and the drawing-name match this SAME part got from parts_ledger.py's covered() — where the surfaces genuinely diverge, the check FAILS honestly rather than being forced green.
Tag | Canonical name | Module | Shape | L (mm) | W (mm) | H (mm) | D (mm) | Volume (m3) | Footprint (m2) | Material | MPN / status | Drawing appearances | Name in BoM (live check) | Name in drawings (live check) | Cell check
D-101 | 3 Phase Power Input | Power distribution | box | 1600 | 860 | 2100 |  | 2.8896 | 1.376 | n/a — not a fabricated part (bought-out assembly) | TDK-Lambda DRB240-24-3-A0 · IDENTIFIED | 5/7 | PASS | PASS | PASS
EP-101 | Main Switchboard | Energy storage source | box | 1600 | 860 | 2100 |  | 2.8896 | 1.376 | n/a — not a fabricated part (bought-out assembly) | Schneider Electric BlokSeT MB301M · IDENTIFIED | 5/7 | PASS | PASS | PASS
EP-102 | Mains Incomer | Energy storage source | box | 1600 | 860 | 2100 |  | 2.8896 | 1.376 | n/a — not a fabricated part (bought-out assembly) | ABB 1SDA067417R1 · IDENTIFIED | 3/7 | PASS | PASS | PASS
EP-103 | SCADA / Plant Control System | Power distribution | box | 700 | 820 | 1800 |  | 1.0332 | 0.574 | n/a — not a fabricated part (bought-out assembly) | process-support system (catalogue class) · SYSTEM | 7/7 | PASS | PASS | PASS
EP-104 | Motor Control Center | Power distribution | box | 1600 | 1020 | 2100 |  | 3.4272 | 1.632 | n/a — not a fabricated part (bought-out assembly) | Eaton Freedom 2100 · IDENTIFIED | 4/7 | PASS | PASS | PASS
G-201 | Standby Diesel Generator | Power distribution | box | 862 | 733 | 948 |  | 0.59899 | 0.63185 | n/a — not a fabricated part (bought-out assembly) | balance-of-plant system (catalogue class) · UTILITY | 4/7 | PASS | PASS | PASS
I-102 | Electrical Control Cabinet | Safety protection | box | 372.5 | 570 | 600 |  | 0.1274 | 0.21232 | structural steel | made to spec (structural) · BESPOKE | 5/7 | PASS | PASS | PASS
I-103 | Digital Control Panel | Control compute communication | box | 372.5 | 570 | 410 |  | 0.087053 | 0.21232 | n/a — not a fabricated part (bought-out assembly) | Siemens 6AV2123-2GB03-0AX0 · IDENTIFIED | 5/7 | PASS | PASS | PASS
M-101 | Distribution Manifold | Mass fluid transport process | cylinder |  |  | 1930 | 372 | 0.20977 | 0.10869 | PVC-U / 304 stainless (WRAS) | requirement stated — parametric · NOT FOUND | 5/7 | PASS | PASS | PASS
P-101 | Ro High Pressure Pump | Mass fluid transport process | box | 600 | 510 | 660 |  | 0.20196 | 0.306 | PVC-U / 304 stainless (WRAS) | Grundfos 96502039 · IDENTIFIED | 7/7 | PASS | PASS | PASS
P-102 | Hand Watering Pump | Mass fluid transport process | box | 900 | 500 | 700 |  | 0.315 | 0.45 | PVC-U / 304 stainless (WRAS) | Grundfos 96935501 · IDENTIFIED | 7/7 | PASS | PASS | PASS
P-103 | Drain Transfer Pump | Mass fluid transport process | box | 600 | 510 | 660 |  | 0.20196 | 0.306 | PVC-U / 304 stainless (WRAS) | Grundfos 96539165 · IDENTIFIED | 6/7 | PASS | PASS | PASS
P-104 | Drain Transfer Pump | Mass fluid transport process | box | 600 | 510 | 660 |  | 0.20196 | 0.306 | PVC-U / 304 stainless (WRAS) | Grundfos SL1.50.65.22.2.50D.C · IDENTIFIED | 7/7 | PASS | PASS | PASS
P-105 | Irrigation Pump | Mass fluid transport process | box | 1379 | 766 | 1073 |  | 1.1334 | 1.0563 | — | — · — | — | PASS | FAIL — canonical name not matched in any drawing surface (0/0 surfaces) | ⚠ FAIL — 'Material' placeholder '—'; 'Drawing appearances' placeholder '—'
P-106 | Fertigation Dosing Pump | Mass fluid transport process | box | 600 | 510 | 660 |  | 0.20196 | 0.306 | PVC-U / 304 stainless (WRAS) | Grundfos 96122012 · IDENTIFIED | 7/7 | PASS | PASS | PASS
P-107 | Fertigation Dosing Pump | Mass fluid transport process | box | 600 | 510 | 660 |  | 0.20196 | 0.306 | PVC-U / 304 stainless (WRAS) (via fold: P-106) | Grundfos 96122012 · IDENTIFIED (via fold: P-106) | 7/7 (via fold: P-106) | PASS | PASS | PASS
TK-101 | Cip Tank | Maintenance serviceability | cylinder |  |  | 1300 | 1400 | 2.0012 | 1.5394 | FRP/GRP | made to spec · BESPOKE | 5/7 | PASS | PASS | PASS
TK-102 | Cleaning Tank | Maintenance serviceability | cylinder |  |  | 1300 | 1400 | 2.0012 | 1.5394 | FRP/GRP | made to spec · BESPOKE | 5/7 | PASS | PASS | PASS
TK-103 | Nutrient Tank | Mass fluid transport process | cylinder |  |  | 1100 | 1100 | 1.0454 | 0.95033 | FRP/GRP | made to spec · BESPOKE | 5/7 | PASS | PASS | PASS
TK-104 | Nutrient Tank | Mass fluid transport process | cylinder |  |  | 1100 | 1100 | 1.0454 | 0.95033 | FRP/GRP (via fold: TK-103) | made to spec · BESPOKE (via fold: TK-103) | 5/7 (via fold: TK-103) | PASS | PASS | PASS
TK-105 | Nutrient Tank | Mass fluid transport process | cylinder |  |  | 1100 | 1100 | 1.0454 | 0.95033 | FRP/GRP (via fold: TK-103) | made to spec · BESPOKE (via fold: TK-103) | 5/7 (via fold: TK-103) | PASS | PASS | PASS
TK-106 | Drain Water Tank | Mass fluid transport process | cylinder |  |  | 3700 | 3700 | 39.7828 | 10.7521 | FRP/GRP | made to spec · BESPOKE | 5/7 | PASS | PASS | PASS
TK-107 | Drain Water Tank | Mass fluid transport process | cylinder |  |  | 3700 | 3700 | 39.7828 | 10.7521 | FRP/GRP (via fold: TK-106) | made to spec · BESPOKE (via fold: TK-106) | 5/7 (via fold: TK-106) | PASS | PASS | PASS
TK-108 | Fresh Water Tank | Mass fluid transport process | cylinder |  |  | 3700 | 3700 | 39.7828 | 10.7521 | FRP/GRP | made to spec · BESPOKE | 5/7 | PASS | PASS | PASS
TK-109 | Nutrient Tank | Mass fluid transport process | cylinder |  |  | 1100 | 1100 | 1.0454 | 0.95033 | FRP/GRP (via fold: TK-103) | made to spec · BESPOKE (via fold: TK-103) | 5/7 (via fold: TK-103) | PASS | PASS | PASS
TK-110 | Nutrient Tank | Mass fluid transport process | cylinder |  |  | 1100 | 1100 | 1.0454 | 0.95033 | FRP/GRP (via fold: TK-103) | made to spec · BESPOKE (via fold: TK-103) | 5/7 (via fold: TK-103) | PASS | PASS | PASS
TK-111 | Nutrient Tank | Mass fluid transport process | cylinder |  |  | 1100 | 1100 | 1.0454 | 0.95033 | FRP/GRP (via fold: TK-103) | made to spec · BESPOKE (via fold: TK-103) | 5/7 (via fold: TK-103) | PASS | PASS | PASS
TK-112 | Nutrient Tank | Mass fluid transport process | cylinder |  |  | 1100 | 1100 | 1.0454 | 0.95033 | FRP/GRP (via fold: TK-103) | made to spec · BESPOKE (via fold: TK-103) | 5/7 (via fold: TK-103) | PASS | PASS | PASS
TK-113 | Nutrient Tank | Mass fluid transport process | cylinder |  |  | 1100 | 1100 | 1.0454 | 0.95033 | FRP/GRP (via fold: TK-103) | made to spec · BESPOKE (via fold: TK-103) | 5/7 (via fold: TK-103) | PASS | PASS | PASS
TK-114 | Drain Collection Sump | Mass fluid transport process | cylinder |  |  | 1400 | 2100 | 4.849 | 3.4636 | FRP/GRP | made to spec · BESPOKE | 5/7 | PASS | PASS | PASS
TK-115 | Drain Collection Sump | Mass fluid transport process | cylinder |  |  | 1400 | 2100 | 4.849 | 3.4636 | FRP/GRP (via fold: TK-114) | made to spec · BESPOKE (via fold: TK-114) | 5/7 (via fold: TK-114) | PASS | PASS | PASS
TX-101 | Transformer | Structure containment | box | 1090 | 927 | 1199 |  | 1.2115 | 1.0104 | n/a — not a fabricated part (bought-out assembly) | requirement stated · NOT FOUND | 3/7 | PASS | PASS | PASS
TX-102 | Distribution Transformer | Power distribution | box | 1090 | 927 | 1199 |  | 1.2115 | 1.0104 | n/a — not a fabricated part (bought-out assembly) | Hammond Power Solutions SG3A0075KB · IDENTIFIED | 3/7 | PASS | PASS | PASS
U-201 | Control + Instrument UPS | Power distribution | box | 600 | 510 | 600 |  | 0.1836 | 0.306 | n/a — not a fabricated part (bought-out assembly) | balance-of-plant system (catalogue class) · UTILITY | 4/7 | PASS | PASS | PASS
V-101 | Gac Filter | Mass fluid transport process | cylinder |  |  | 1400 | 1300 | 1.8583 | 1.3273 | PVC-U / 304 stainless (WRAS) | General Carbon HP-1000 · IDENTIFIED | 6/7 | PASS | PASS | PASS
V-102 | Uv Disinfection | Mass fluid transport process | cylinder |  |  | 1098.4 | 1830 | 2.889 | 2.6302 | PVC-U / 304 stainless (WRAS) | WEDECO (Xylem) Spektron 30e · IDENTIFIED | 7/7 | PASS | PASS | PASS
V-103 | Gac Softener | Mass fluid transport process | cylinder |  |  | 1800 | 900 | 1.1451 | 0.63617 | n/a — not a fabricated part (bought-out assembly) | Pentair Structural 36X72 COMP 6"TF 6"BF · IDENTIFIED | 5/7 | PASS | PASS | PASS
V-104 | Cloth Filter | Mass fluid transport process | cylinder |  |  | 2877.8 | 1133 | 2.9014 | 1.0082 | structural steel | made to spec (structural) · BESPOKE | 7/7 | PASS | PASS | PASS
V-105 | Cloth Filter | Mass fluid transport process | cylinder |  |  | 2877.8 | 1133 | 2.9014 | 1.0082 | structural steel (via fold: V-104) | made to spec (structural) · BESPOKE (via fold: V-104) | 7/7 (via fold: V-104) | PASS | PASS | PASS
V-106 | Softener Vessel | Mass fluid transport process | cylinder |  |  | 1300 | 1200 | 1.4703 | 1.131 | carbon steel | made to spec · BESPOKE | 5/7 | PASS | PASS | PASS
V-107 | Softener Vessel | Mass fluid transport process | cylinder |  |  | 1300 | 1200 | 1.4703 | 1.131 | PVC-U / 304 stainless (WRAS) | Sensata Technologies, Inc. SOL7A4 · IDENTIFIED | 5/7 | PASS | PASS | PASS
X-102 | Electrical Control Panel | Power distribution | box | 1000 | 1220 | 1100 |  | 1.342 | 1.22 | — | — · — | — | PASS | FAIL — canonical name not matched in any drawing surface (0/0 surfaces) | ⚠ FAIL — 'Material' placeholder '—'; 'Drawing appearances' placeholder '—'
X-103 | Concentrate Outlet | Environmental interface | box | 1000 | 1060 | 1100 |  | 1.166 | 1.06 | — | — · — | — | PASS | FAIL — canonical name not matched in any drawing surface (0/0 surfaces) | ⚠ FAIL — 'Material' placeholder '—'; 'Drawing appearances' placeholder '—'
X-104 | Permeate Outlet | Environmental interface | box | 2030 | 1060 | 1100 |  | 2.367 | 2.1518 | n/a — not a fabricated part (bought-out assembly) | Rittal 1180.000 · IDENTIFIED | 5/7 | PASS | PASS | PASS
Z-101 | Reverse Osmosis Skid | Mass fluid transport process | box | 3230 | 1500 | 1600 |  | 7.752 | 4.845 | structural steel | made to spec (structural) · BESPOKE | 5/7 | PASS | PASS | PASS
Z-102 | Uf Module Bank | Mass fluid transport process | box | 3230 | 1500 | 1600 |  | 7.752 | 4.845 | n/a — not a fabricated part (bought-out assembly) | requirement stated · MERGED·SYNONYM | 5/7 | PASS | PASS | PASS
Z-103 | Ultrafiltration Module | Mass fluid transport process | box | 3230 | 1500 | 1600 |  | 7.752 | 4.845 | n/a — not a fabricated part (bought-out assembly) | requirement stated · MERGED·SYNONYM | 3/7 | PASS | PASS | PASS

## Overview
ForgeOS Review Workbook — fischer-codema-v79 |  |  |  | ↑ Contents
⬤ TAB QUALITY 10/10 · PASS (target ≥8, live from the Quality & Audit score cell) · dashboard integrity (every quoted number vs its engine source) — section scores match the engine scorecard 14/14; capex category % = 100 × £ / Σ (per-row arithmetic) 10/… · full audit: Quality & Audit tab
Live Excel review surface. Yellow cells are editable inputs; green cells are live formulas that recompute downstream. See the '⚠ Checks' tab for invariants that go RED where the engine's numbers do not reconcile.
Run provenance
Run directory | fischer-codema-v79
Git short SHA | 2ddf4dd58
State saved at | 2026-07-04T19:25:20.288Z
Project id | chain-v2-1783193120288
Product class | water_treatment
Quality scorecard
VERDICT: SHIPS · floor 9/10 (min of every DETERMINISTIC section & non-mirror tab — live cells on Quality & Audit; the LLM self-audit is advisory and never floors; ships at ≥8 everywhere)
Deterministic gate floor (min gate section) | 10
Mean (all sections) | 10
Deterministic gates ≥8 | 8/8
Iteration | 0
Section | Score | ≥8? | Defects | Cell check
Sections marked (advisory) are the LLM self-audit — non-gating; amber = advisory concern, red = a deterministic gate breach.
Headline (advisory) | 9 | PASS |  | PASS
Brief compliance (advisory) | 6 | ADVISORY | 4 unverified constraints; 1 failing constraint (storage) | PASS
Bill of materials (advisory) | 8 | PASS |  | PASS
Performance card (advisory) | 9 | PASS |  | PASS
Design narrative (advisory) | 8 | PASS |  | PASS
Physics fidelity (advisory) | 5 | ADVISORY | high-severity motor/vessel sizing discrepancies; part_realism=5 | PASS
Drawing gates | 10 | PASS |  | PASS
Cost sanity | 10 | PASS |  | PASS
Physics gates | 10 | PASS |  | PASS
Tool archetype | 10 | PASS |  | PASS
Connectivity | 10 | PASS | X-107 Circuit Breakers: missing_input — Electrical component with no upstream power supply.; X-107 Circuit Breakers: missing_output — Electrical component with no downstream load.; X-110 Circuit Breaker: missing_input — Electrical component with no upstream power supply.; X-110 Circuit Breaker: missing_output — Electrical component with no downstream load.; X-114 PLC Controller: orphan_controller — Controller with no signal connections — not wired to anything it controls.; X-115 Veolia Ro40 Controller: orphan_controller — Controller with no signal connections — not wired to anything it controls.; X-118 Hoogendoorn iSii Remote Monitoring: orphan_controller — Controller with no signal connections — not wired to anything it controls.; X-119 Dc3 Power Controller: orphan_controller — Controller with no signal connections — not wired to anything it controls.; X-120 HMI Touchscreen: orphan_controller — Controller with no signal connections — not wired to anything it controls.; X-121 Siemens S7 1200 PLC: orphan_controller — Controller with no signal connections — not wired to anything it controls.; X-123 Remote Monitoring Gateway: orphan_controller — Controller with no signal connections — not wired to anything it controls.; I-103 Digital Control Panel: missing_output — Electrical component with no downstream load.; EP-102 Mains Incomer: missing_input — Battery-limit origin with no upstream feed drawn — the TYPE classifier has no pattern for this part, but its name names an origin boundary that still needs its fe; X-128 Power Supply Unit: orphan_controller — Controller with no signal connections — not wired to anything it controls.; TX-101 Transformer: missing_input — Electrical component with no upstream power supply.; TX-101 Transformer: missing_output — Electrical component with no downstream load.; X-143 Zoned distribution — department delivery mains: missing_input — Battery-limit origin with no upstream feed drawn — the TYPE classifier has no pattern for this part, but its name names an origin; X-146 Zoned distribution — drain/return risers (gravity): missing_output — Battery-limit sink/drain with no downstream connection drawn — where does this discharge to? The TYPE classifier has no patte; X-147 Zoned distribution — drain collection lines: missing_output — Battery-limit sink/drain with no downstream connection drawn — where does this discharge to? The TYPE classifier has no pattern for; X-148 Zoned distribution — main drain headers: missing_output — Battery-limit sink/drain with no downstream connection drawn — where does this discharge to? The TYPE classifier has no pattern for this; ... and 1 more connectivity concerns | PASS
Brief compliance | 10 | PASS |  | PASS
Unresolved critic highs | 10 | PASS |  | PASS
Physics fidelity | 10 | PASS | advisory: the LLM critic's own physics opinion is 7/10 — an annotation only, it never scores (B3); advisory: 4 uncorroborated critic note(s) render as advisory notes — visible, never scored | PASS
Computational checks
Deterministic invariants | 130 / 130 pass · 0 FAIL | full detail on the ⚠ Checks tab
Headline metrics
Metric | Value | Unit | Notes / source | Cell check
Irrigation Demand M3 Per | 45 | m3/h | Primary deliverable taken directly from the brief target (parsedBrief.constraints.target_performance). No per-class headline deriver yet for "water_treatment"; surfaced from the brief so the headline is never blank. | PASS
Unit cost ceiling | 1,400,000 | GBP | Brief cost ceiling per unit. | PASS
Cultivation Containers | 6,000 | count | Brief target metric (scale). | PASS
Ro Permeate Capacity M3 Per | 8 | m3/h | Brief target metric (scale). | PASS
Ro Recovery | 75 | % | Brief target metric (efficiency). | PASS
Water Storage Capacity | 120 | m3 | Brief target metric (scale). | PASS
Actuated Valves | 200 | count | Brief target metric (scale). | PASS
Where the money goes — capex by category
Deterministic roll-up of every bill-of-materials line, grouped by equipment category. Sums to the bill-of-materials grand total.
Category | Cost (£) | % of capex | Share | Cell check
Pipework & valves | 339593 | 41.6 | █████████████████ | PASS
Filtration & membranes | 111964 | 13.7 | █████ | PASS
Controls & instrumentation | 110691 | 13.6 | █████ | PASS
Vessels, tanks & columns | 108361 | 13.3 | █████ | PASS
Other equipment | 65562 | 8 | ███ | PASS
Rotating equipment | 35261 | 4.3 | ██ | PASS
Power & electrical | 34221 | 4.2 | ██ | PASS
Enclosure | 10011 | 1.2 | ▏ | PASS
Structure & skids | 120 | 0 | ▏ | PASS
Cabling & power runs | 53 | 0 | ▏ | PASS
Total (bill of materials) | 815837

## Renders
Renders — photoreal views of the plant | ↑ Contents
⬤ TAB QUALITY 10/10 · PASS (target ≥8, live from the Quality & Audit score cell) · render mechanism: parts-ledger coverage × default-size litter × typed-shape × vision-critic verdict (render-vision-critique.json) — drawing part coverage (blender) 27/27… · full audit: Quality & Audit tab
The informative views from the Blender scene build: interior hero isometric, annotated interior plan, and the building exterior. Every rendered view file (including the additional corner angles) is listed with its caption on the Drawings register tab; the full-resolution files live in the run folder. |  | SG: All pipework seems to be above ground whereas a lot of this pipework may be better placed below ground in normal circumstances, and indeed a lot would have to be underground for drainage.
SG: Some pipes look weirdly big, hard to deduce much from the images in terms of pipe runs etc. Labels don't seem clear in terms of what they are referring to.
Render 1 — Interior iso |  | SG: Usually what would be more useful/important for the design is a working schematic which pipe runs, sizes, valve locations etc, would show how everything connects better.
Interior render — three-quarter hero perspective · plant envelope 22.1 × 27.0 × 4.5 m · principal equipment: TK-106 Drain Water Tank · TK-107 Drain Water Tank · TK-108 Fresh Water Tank · Z-101 Reverse Osmosis Skid · Z-102 Uf Module Bank
Render 2 — Interior plan
Interior render — plan view, looking down · plant envelope 22.1 × 27.0 × 4.5 m · principal equipment: TK-106 Drain Water Tank · TK-107 Drain Water Tank · TK-108 Fresh Water Tank · Z-101 Reverse Osmosis Skid · Z-102 Uf Module Bank
Render 5 — Exterior iso
Exterior render — three-quarter hero perspective · plant envelope 22.1 × 27.0 × 4.5 m · building shell + site apron (equipment enclosed)
Render 7 — Exterior FR iso
Exterior render — front-right corner perspective · plant envelope 22.1 × 27.0 × 4.5 m · building shell + site apron (equipment enclosed)

## Cost waterfall
Cost waterfall — BoM → installed ASP | [7 empty] | ↑ Contents
⬤ TAB QUALITY 10/10 · PASS (target ≥8, live from the Quality & Audit score cell) · cost-waterfall arithmetic ties (each step vs its named costStack anchor; sums close) — waterfall rows tie live to their stated costStack anchor 6/6; assembly/install row… · full audit: Quality & Audit tab
Running build-up. Yellow = editable step £; the Running total column is LIVE (each = previous running + this step), so Σ bars = total by construction and editing any step recomputes the installed price. The assembly (B6) and installation (B9) bars are ENGINEERING ESTIMATES derived from the bill's own class subtotals × Lang/Hand-style install factors (derivation table below, sources per line) — never bare numbers. 'costStack anchor' shows the engine's stored figure at each milestone so any divergence is visible.
Step | Step £ (editable) | Running total £ (live) | Basis / derivation (costStack anchor for cross-check) | Cell check
Raw materials (BoM) | 815837 | 815837 | ​= Σ Bill of Materials (Ledger) line £ — LIVE link to the bill; edit the bill and this recomputes · engine anchor £800,361 | PASS |  | SG: Hard to check pricing without obtaining actual quotes with todays pricing as a check.
​+ Assembly / erection labour | 115627.11 | 931464.11 | ESTIMATE — Σ BoM class subtotals × assembly-&-integration factor: Vessels & tanks 0.10 · Piping & fittings 0.08 · Rotating machinery 0.15 · Electrical & power 0.20 · Instruments, valves & controls 0.10 · Structural & civil 0.05 · Other equipment 0.10 (LIVE from the derivation table below; Lang/Hand-style factors, sources per line). Engine assembly_labour_gbp kept as anchor · engine anchor £320,144 | PASS
​= Factory COGS |  | 931464.11 | factory_cogs_gbp (anchor — compare running total) · engine anchor £1,120,505 | PASS
​= OEM transfer price |  | 931464.11 | oem_transfer_price_gbp (anchor) · engine anchor £1,120,505 | PASS
​+ Installation / field erection | 315706.95 | 1247171.06 | ESTIMATE — Σ BoM class subtotals × install factor: Vessels & tanks 0.45 · Piping & fittings 0.60 · Rotating machinery 0.30 · Electrical & power 0.35 · Instruments, valves & controls 0.40 · Structural & civil 0.50 · Other equipment 0.30 (LIVE from the derivation table below; Lang/Hand-style factors, sources per line). Engine installation_cost_gbp kept as anchor · engine anchor £240,108 | PASS
​= Installed ASP (process equipment) |  | 1247171.06 | installed_asp_gbp (anchor — process plant installed price) · engine anchor £1,360,613 | PASS
B6 / B9 derivation — BoM class subtotals × Lang/Hand-style factors (Lang 1948 · Hand 1958 · Peters/Timmerhaus/West 5e Tbl 6-5 · Towler & Sinnott)
Equipment class | BoM subtotal £ | Lines / mass | Factor source (assembly + install) | Assembly f | Assembly £ (live) | Install f | Install £ (live) | Cell check
Vessels & tanks | 111788 | 8 line(s) · 3,448 kg | vessel/tank setting + field erection ≈ 40–50% of purchased (P,T&W 5e Tbl 6-5 install 25–55%; Hand 1958 vessel family) | 0.1 | 11178.8 | 0.45 | 50304.6 | PASS
Piping & fittings | 65312 | 50 line(s) | pipework erection is the labour-dominant field trade ≈ 50–70% of material (Towler & Sinnott piping factor; P,T&W 5e) | 0.08 | 5224.96 | 0.6 | 39187.2 | PASS
Rotating machinery | 39827 | 7 line(s) | machine setting, alignment + commissioning ≈ 25–60% of purchased, mid 30% (P,T&W 5e Tbl 6-5; Hand 1958 pump family) | 0.15 | 5974.05 | 0.3 | 11948.1 | PASS
Electrical & power | 338153 | 46 line(s) | panel wiring/integration ~20%; field electrical (containment, pulling, termination, test) ≈ 15–40% (P,T&W 5e; Towler & Sinnott f_el) | 0.2 | 67630.6 | 0.35 | 118353.55 | PASS
Instruments, valves & controls | 158584 | 27 line(s) | instrument mounting, hook-up, loop check + calibration ≈ 30–50% (Towler & Sinnott f_i; ISA installation norms) | 0.1 | 15858.4 | 0.4 | 63433.6 | PASS
Structural & civil | 9140 | 5 line(s) | steelwork trial-fit ~5%; site erection ≈ 50% of fabricated-steel cost (UK structural-erection norms; P,T&W civil factors) | 0.05 | 457 | 0.5 | 4570 | PASS | SG: Seems very low for civils. Usually irrigation would require a lot of civils unless specifically goiong in an existing building where no underground works are allowed.
Other equipment | 93033 | 30 line(s) | ASSUMPTION — no class signal on these lines; generic process-equipment install 30% (P,T&W 5e 25–55% band, low end) + 10% assembly | 0.1 | 9303.3 | 0.3 | 27909.9 | PASS
Σ — feeds the ladder: B6 = ΣF, B9 = ΣH (live) | 815837 |  |  |  | 115627.11 |  | 315706.95
Reconciliation: Σ bars = the ladder's running total by construction (col C is live off col B; B6/B9 are live off this table). The engine's costStack anchors (assembly £320,144 · install £240,108 — blanket class factors) are shown per bar for cross-check; a divergence between the class-derived estimate and the blanket anchor is DISCLOSED, never hidden.

## Financial model
Financial model — cost of service first · speculative model in the appendix | [7 empty] | ↑ Contents
⬤ TAB QUALITY 10/10 · PASS (target ≥8, live from the Quality & Audit score cell) · formula integrity (cells reference drivers; no orphan literals) + scenario arithmetic (live) — model value cells are live formulas or declared (yellow) inputs 225/226; c… · full audit: Quality & Audit tab
THE VALID FRAME LEADS: this plant is a cost subsystem, so the tab opens with its lifecycle cost-of-service model (capex + opex + levelised £/unit), every cell live over the yellow 'Inputs & Assumptions' tab. The revenue/EBITDA/NPV/IRR machinery survives only as a clearly-labelled APPENDIX at the bottom — one caveat, stated once. Money £#,##0; margins 0.0%; years 0.0.
COST-OF-SERVICE MODEL — the lifecycle cost of the delivered service
Levelised cost of delivered output = (capex annualised at CRF 0.117 over 20 yr + annual opex) ÷ annual delivered volume (engine primary output metric (45 m3/h)). Every value cell is a LIVE formula over the yellow Inputs & Assumptions drivers — edit an input and this recomputes.
Item | Value (£) |  | Basis | Cell check
All-in capex | 1360613 |  | live from Inputs — installed capex (engine costStack all-in / installed ASP) | PASS
Annualised capex / yr | 159817.0924 |  | capex × CRF (live off the Inputs discount rate + project life; as-built i=10%, n=20 yr) | PASS
Energy / yr | 41340 |  | live from Inputs — connected load × hours × ELECTRICAL load factor × £/kWh (as-built 53 kW × 8,000 h × 65% × £0.15/kWh) | PASS |  | SG: Could be too high.A lot of kit e.g. pumps may only operate infrequently. What else is causing the high energy use? £41k is a lot.
Maintenance / yr | 40818.39 |  | live from Inputs — 3% of capex/yr | PASS
Labour + other opex / yr | 52212 |  | live from Inputs — labour £25,000 + other opex £27,212 (the Inputs basis: unmanned/skid plant unless a headcount signal exists) | PASS
TOTAL annual opex / yr | 134370.39 |  | energy + maintenance + labour + other (sum of the live rows above)
Annual delivered volume (m3/h) | 45 |  | engine primary output metric (45 m3/h) | PASS
LEVELISED COST (£/m3) | 6537.4996 |  | (annualised capex + total opex) ÷ annual delivered volume — live; as-built £6,537.50/m3 over 45 m3/h | PASS
Sweet spot & brief reconciliation
Reconciliation verdict — COMPATIBLE — the brief's cost ceiling and output target fit together
The brief is internally consistent: 360,000 m³/yr fits within the £1.40M ceiling. Recommended operating point: 360,000 m³/yr at £623k (£2/m³/yr). Objective: BALANCED (the best cost/output compromise).
Primary objective followed: BALANCED — the best cost/output compromise
Recommended operating point | Value | [6 empty] | Cell check
Reference output — tool snapshot (Q_ref) | 360000 | [6 empty] | PASS
Reference capex, ex-works — tool snapshot (Q_ref) | 623277.84 | [6 empty] | PASS
Capacity-scaling exponent (n) | 0.65 | [6 empty] | PASS
Recommended output (m³/yr) | 360000 | [6 empty] | PASS
Recommended capex (£) | 623278 | [6 empty] | PASS
Recommended £/m³/yr | 1.7313 | [6 empty] | PASS
Recommended scale vs brief (×) | 1 | [6 empty] | PASS
Within cost ceiling? | Yes | [6 empty] | PASS
Meets hard output floor? | Yes | [6 empty] | PASS
Cost–output frontier (capacity-scaling law) — £/unit falls with scale (economies of scale)
Output (m³/yr) | Capex (£) | £/m³/yr | [5 empty] | Cell check
90000 | 253129 | 2.8125 | [5 empty] | PASS
113392.8945 | 294148 | 2.5941 | [5 empty] | PASS
142866.0947 | 341813 | 2.3925 | [5 empty] | PASS
180000 | 397203 | 2.2067 | [5 empty] | PASS
226785.789 | 461568 | 2.0353 | [5 empty] | PASS
285732.1894 | 536363 | 1.8772 | [5 empty] | PASS
360000 | 623278 | 1.7313 | [5 empty] | PASS
453571.578 | 724277 | 1.5968 | [5 empty] | PASS
571464.3787 | 841643 | 1.4728 | [5 empty] | PASS
720000 | 978028 | 1.3584 | [5 empty] | PASS
907143.1559 | 1136513 | 1.2528 | [5 empty] | PASS
1142928.7574 | 1320680 | 1.1555 | [5 empty] | PASS
1440000 | 1534690 | 1.0658 | [5 empty] | PASS
APPENDIX — if the output were sold (speculative — not the valid frame for this plant)
⚠ SPECULATIVE APPENDIX — no per-unit market sale price is derivable for this product class, so every revenue / EBITDA / NPV / IRR figure below is NOT a valid investor model until a real sale price is entered on the 'Inputs & Assumptions' tab. This caveat is stated ONCE and covers the whole appendix.
Economics — base case (revenue / opex / EBITDA / NPV / IRR)
Annual profit & loss
Line | £ / yr (live) | Unit | Formula | Cell check
Annual revenue | 0 | £/yr | output × sale price (£/unit) | PASS
Consumables — dosing chemicals · nutrient / fertiliser stock · filter media & membranes | 0 | £/yr | output × consumable-intensity ratio × consumables price — the classes are the plant's own (from its process/media BoM + contract lines); price them on the Inputs tab | PASS
Energy cost | 41340 | £/yr | connected load (kW) × hours × load factor × £/kWh | PASS
Labour | 25000 | £/yr | from inputs | PASS
Maintenance | 40818.39 | £/yr | capex × maint% / 100 | PASS
Other opex | 27212 | £/yr | from inputs | PASS
Total opex | 134370.39 | £/yr | Σ feed + energy + labour + maintenance + other
EBITDA | -134370.39 | £/yr | revenue − total opex | PASS
Headline metrics (live)
EBITDA margin | n/a — no revenue basis |  | EBITDA ÷ revenue
Simple payback | n/a (EBITDA≤0) | yr | capex ÷ EBITDA (only if EBITDA > 0)
Discounted cashflow — NPV & IRR (live)
Year | Cashflow £ (live) | Discounted £ (live) | Note | Cell check
0 | -1360613 | -1360613 | capex outflow | PASS
1 | -134370.39 | -122154.9 | EBITDA inflow (within project life) | PASS
2 | -134370.39 | -111049.9091 | EBITDA inflow (within project life) | PASS
3 | -134370.39 | -100954.4628 | EBITDA inflow (within project life) | PASS
4 | -134370.39 | -91776.7844 | EBITDA inflow (within project life) | PASS
5 | -134370.39 | -83433.4403 | EBITDA inflow (within project life) | PASS
6 | -134370.39 | -75848.5821 | EBITDA inflow (within project life) | PASS
7 | -134370.39 | -68953.2565 | EBITDA inflow (within project life) | PASS
8 | -134370.39 | -62684.7786 | EBITDA inflow (within project life) | PASS
9 | -134370.39 | -56986.1624 | EBITDA inflow (within project life) | PASS
10 | -134370.39 | -51805.6022 | EBITDA inflow (within project life) | PASS
11 | -134370.39 | -47096.002 | EBITDA inflow (within project life) | PASS
12 | -134370.39 | -42814.5472 | EBITDA inflow (within project life) | PASS
13 | -134370.39 | -38922.3157 | EBITDA inflow (within project life) | PASS
14 | -134370.39 | -35383.9233 | EBITDA inflow (within project life) | PASS
15 | -134370.39 | -32167.203 | EBITDA inflow (within project life) | PASS
16 | -134370.39 | -29242.9119 | EBITDA inflow (within project life) | PASS
17 | -134370.39 | -26584.4653 | EBITDA inflow (within project life) | PASS
18 | -134370.39 | -24167.6957 | EBITDA inflow (within project life) | PASS
19 | -134370.39 | -21970.6325 | EBITDA inflow (within project life) | PASS
20 | -134370.39 | -19973.3023 | EBITDA inflow (within project life) | PASS
NPV |  | -2504583.8773 | Σ discounted cashflow (capex at yr 0 + discounted EBITDA) | PASS
IRR |  | n/a — no revenue basis | live =IRR over the year-0..N cashflow row (text n/a when the cashflow never turns positive) | PASS
Opex breakdown (feeds the pie chart)
Driver | £ / yr (live) | % of opex (live) |  | Cell check
Consumables — dosing chemicals · nutrient / fertiliser stock | 0 | 0% |  | PASS
Energy | 41340 | 30.77% |  | PASS
Labour | 25000 | 18.61% |  | PASS
Maintenance | 40818.39 | 30.38% |  | PASS
Other | 27212 | 20.25% |  | PASS
Revenue | 0
Total opex | 134370.39
EBITDA | -134370.39
Scenarios — scale sweep & price sensitivity
Output sweep (output, m3/h) — capex via the tunable scaling exponent (default linear/modular); payback / NPV / IRR live per row
Output (m3/h) | Capex £ (live) | Revenue £ (live) | Total opex £ (live) | EBITDA £ (live) | Payback yr | NPV £ (live) | IRR (live) | Cell check
9 | 272122.6 | 0 | 68643.678 | -68643.678 | n/a | -856524.9266 | n/a | PASS
11.1542 | 337256.6561 | 0 | 72576.6914 | -72576.6914 | n/a | -955142.943 | n/a | PASS
13.824 | 417980.3136 | 0 | 77451.0574 | -77451.0574 | n/a | -1077364.826 | n/a | PASS
17.1329 | 518027.6993 | 0 | 83492.2551 | -83492.2551 | n/a | -1228844.3333 | n/a | PASS
21.2337 | 642018.8502 | 0 | 90979.2579 | -90979.2579 | n/a | -1416576.5595 | n/a | PASS
26.3162 | 795692.5296 | 0 | 100258.5916 | -100258.5916 | n/a | -1649250.4378 | n/a | PASS
32.6151 | 986145.0901 | 0 | 111758.7579 | -111758.7579 | n/a | -1937610.3968 | n/a | PASS
40.4217 | 1222184.2334 | 0 | 126011.5954 | -126011.5954 | n/a | -2294991.9803 | n/a | PASS
50.0969 | 1514722.0755 | 0 | 143676.0144 | -143676.0144 | n/a | -2737916.9791 | n/a | PASS
62.0878 | 1877277.0627 | 0 | 165568.3041 | -165568.3041 | n/a | -3286853.37 | n/a | PASS
76.9489 | 2326614.9706 | 0 | 192700.8386 | -192700.8386 | n/a | -3967185.8387 | n/a | PASS
95.3671 | 2883504.8007 | 0 | 226327.7199 | -226327.7199 | n/a | -4810360.2655 | n/a | PASS
118.1938 | 3573689.3511 | 0 | 268003.3848 | -268003.3848 | n/a | -5855353.2447 | n/a | PASS
146.4841 | 4429070.4612 | 0 | 319654.1737 | -319654.1737 | n/a | -7150466.6373 | n/a | PASS
181.5459 | 5489193.5919 | 0 | 383667.9746 | -383667.9746 | n/a | -8755575.3406 | n/a | PASS
225 | 6803065 | 0 | 463003.95 | -463003.95 | n/a | -10744878.6308 | n/a | PASS
Chart helper — payback capped at 40 yr (text 'n/a' breaks a chart series)
Output (m3/h) | Payback yr (chart) | [6 empty] | Cell check
9 | 40 | [6 empty] | PASS
11.1542 | 40 | [6 empty] | PASS
13.824 | 40 | [6 empty] | PASS
17.1329 | 40 | [6 empty] | PASS
21.2337 | 40 | [6 empty] | PASS
26.3162 | 40 | [6 empty] | PASS
32.6151 | 40 | [6 empty] | PASS
40.4217 | 40 | [6 empty] | PASS
50.0969 | 40 | [6 empty] | PASS
62.0878 | 40 | [6 empty] | PASS
76.9489 | 40 | [6 empty] | PASS
95.3671 | 40 | [6 empty] | PASS
118.1938 | 40 | [6 empty] | PASS
146.4841 | 40 | [6 empty] | PASS
181.5459 | 40 | [6 empty] | PASS
225 | 40 | [6 empty] | PASS
Low / Central / High — sale price ±25%, energy ±25%, capex ±15% (at the base output)
Driver / metric | Low | Central | High |  |  |  |  | Cell check
Sale price (±25%) | 0 | 0 | 0 |  |  |  |  | PASS
Energy price (±25%) | 0.1125 | 0.15 | 0.1875 |  |  |  |  | PASS
Capex (±15%) | 1156521.05 | 1360613 | 1564704.95 |  |  |  |  | PASS
Revenue £ (live) | 0 | 0 | 0 |  |  |  |  | PASS
Total opex £ (live) | 117912.6315 | 134370.39 | 150828.1485
EBITDA £ (live) | -150828.1485 | -134370.39 | -117912.6315 |  |  |  |  | PASS
Payback yr (live) | n/a | n/a | n/a |  |  |  |  | PASS
What-if sensitivity — one driver at a time (±20%), with the EBITDA swing (tornado magnitude); held at the base output
Driver (±20%) | EBITDA @ −20% | EBITDA @ base | EBITDA @ +20% | Swing £ (¦+20 − −20¦) |  |  |  | Cell check
Sale price | -134370.39 | -134370.39 | -134370.39 | 0 |  |  |  | PASS
Consumables price (dosing chemicals · nutrient / fertiliser stock · filter media & membranes) | -134370.39 | -134370.39 | -134370.39 | 0 |  |  |  | PASS
Consumable intensity ratio | -134370.39 | -134370.39 | -134370.39 | 0 |  |  |  | PASS
Energy price | -126102.39 | -134370.39 | -142638.39 | 16536 |  |  |  | PASS
Capex (→ maintenance) | -126206.712 | -134370.39 | -142534.068 | 16327.356 |  |  |  | PASS
Labour | -129370.39 | -134370.39 | -139370.39 | 10000 |  |  |  | PASS
Breakeven & combined corners (live)
Breakeven sale price (£/unit) | 2986.0087 | EBITDA = 0 at this price (vs the Inputs price)
Combined corners → EBITDA £ | Worst | Base | Best
EBITDA (all drivers swung together) | -148761.1485 | -134370.39 | -119979.6315
Low | -150828.1485
Investment analysis — the sweet-spot finder
High | -117912.6315
★ CAPEX → MAX OUTPUT — type a capex budget in the yellow cell; read the biggest plant it buys + its economics (via the tunable scaling exponent)
Capex budget (EDIT me) £ | 1360613
→ Max production (m3/h) | 45
→ Revenue / yr £ | 0
→ Operating cost / yr £ (interp. from sweep) | 134370.39
→ EBITDA / yr £ | -134370.39
→ Simple payback (yr) | n/a (EBITDA ≤ 0)
→ IRR (annuity) | n/a
DEPLOYMENT VERDICT
NO DEPLOYMENT RECOMMENDED — EBITDA is negative at every scale in the 0.2x–5x sweep at the current inputs (no revenue basis), so there is no point worth deploying capital into. The valid economics for this plant are the cost-of-service model at the top of this tab.
Sweet-spot thresholds — live over the scale sweep (Scenarios tab)
What | Output (m3/h) | Capex £ | IRR | Payback yr | How it's found | Cell check
Break-even scale (EBITDA ≥ 0) | none in range (all EBITDA < 0) | — | — | — | first sweep row with EBITDA ≥ 0 (EBITDA rises with scale); 'none in range' when every sweep row is loss-making
Viability threshold (IRR ≥ discount rate) | > range | — | — | — | first row whose IRR clears the discount rate — capital just covers its cost | ⚠ FAIL — a required cell is empty/placeholder or wrong type
Investable scale (IRR ≥ hurdle) | > range | — | — | — | first row whose IRR clears the editable investor hurdle (Inputs tab) — the SWEET SPOT | ⚠ FAIL — a required cell is empty/placeholder or wrong type
NPV-max scale (in range) | 9 | 272122.6 | n/a | n/a | output that maximises NPV across the sweep (trends to the top of the range when economics improve with scale) | PASS
What moves the sweet spot
The SALE PRICE per output unit is the dominant lever (revenue is linear in it and in output). ENERGY price + connected load set the largest variable-opex line. CAPEX and its six-tenths exponent set the absolute investment and the maintenance line. Flex these on the Inputs tab — every threshold + curve moves live.
[7 empty] | Capex £ | Output m3/h | IRR | Discount-rate line | Hurdle line | NPV £ | Payback yr (cap 40) | EBITDA margin
[7 empty] | 272122.6 | 9 | 0% | 10% | 15% | -856524.9266 | 40 | 0%
[7 empty] | 337256.6561 | 11.1542 | 0% | 10% | 15% | -955142.943 | 40 | 0%
[7 empty] | 417980.3136 | 13.824 | 0% | 10% | 15% | -1077364.826 | 40 | 0%
[7 empty] | 518027.6993 | 17.1329 | 0% | 10% | 15% | -1228844.3333 | 40 | 0%
[7 empty] | 642018.8502 | 21.2337 | 0% | 10% | 15% | -1416576.5595 | 40 | 0%
[7 empty] | 795692.5296 | 26.3162 | 0% | 10% | 15% | -1649250.4378 | 40 | 0%
[7 empty] | 986145.0901 | 32.6151 | 0% | 10% | 15% | -1937610.3968 | 40 | 0%
[7 empty] | 1222184.2334 | 40.4217 | 0% | 10% | 15% | -2294991.9803 | 40 | 0%
[7 empty] | 1514722.0755 | 50.0969 | 0% | 10% | 15% | -2737916.9791 | 40 | 0%
[7 empty] | 1877277.0627 | 62.0878 | 0% | 10% | 15% | -3286853.37 | 40 | 0%
[7 empty] | 2326614.9706 | 76.9489 | 0% | 10% | 15% | -3967185.8387 | 40 | 0%
[7 empty] | 2883504.8007 | 95.3671 | 0% | 10% | 15% | -4810360.2655 | 40 | 0%
[7 empty] | 3573689.3511 | 118.1938 | 0% | 10% | 15% | -5855353.2447 | 40 | 0%
[7 empty] | 4429070.4612 | 146.4841 | 0% | 10% | 15% | -7150466.6373 | 40 | 0%
[7 empty] | 5489193.5919 | 181.5459 | 0% | 10% | 15% | -8755575.3406 | 40 | 0%
[7 empty] | 6803065 | 225 | 0% | 10% | 15% | -10744878.6308 | 40 | 0%
Note on B26: TOOL NODE — deriveOutputDenominator() (independent-cost-sanity-audit.ts) v1, captured by sweet-spot.ts::reconcile() v1 (Phase 1, 2026-06-24) at the reconciliation pipeline stage. Input consumed: parsedBrief.constraints.target_performance (the brief's primary scale metric, annualised). Frozen at capture time — recompute requires an engine re-run.
Note on B27: TOOL NODE — readHeadlineCostGbp() (independent-cost-sanity-audit.ts) v1, source 'costStack.ex_works', captured by sweet-spot.ts::reconcile() v1 at the reconciliation pipeline stage. MAY differ from the Cost waterfall tab's current total if the plant was re-costed after reconciliation ran. Frozen at capture time — recompute requires an engine re-run.
Note on B29: TOOL NODE — sweet-spot.ts::reconcile() v1 (Phase 1, 2026-06-24): the reconciliation algorithm's CHOSEN operating point given the brief's objective (balanced) and verdict (compatible) — a branchy decision, not a closed-form recompute. Inputs consumed: reference output (B26), reference capex (B27), cost ceiling (INP_UNIT_COST_CEILING). Recompute requires an engine re-run.

## Bill of Materials (Ledger)
Bill of Materials (Ledger) | [14 empty] | ↑ Contents
⬤ TAB QUALITY 9.9/10 · PASS (target ≥8, live from the Quality & Audit score cell) · column-contract arithmetic: 10 × 417/417 rows passing; content checks: BoM ledger column contract (per-row Row check) — cell completeness+type contract 2895/2917 · score… · full audit: Quality & Audit tab
THE BILL + its provenance + its engineering, on one sheet — ALL COLUMNS VISIBLE (nothing hidden/collapsed). Buy-list: tag · item · qty · unit £ · LIVE line £. 'Cost basis' (cols F–J) = HOW each £ was derived (method / inputs / factors / estimate class / confidence); 'Engineering spec' (cols K–N) = WHY each principal is this size (duty / material / sizing calc / MPN). Σ line £ is live at the foot; commodity lines leave the spec columns blank (correct — they need no sizing basis). ↳ SUB-COMPONENT ROWS are grouped under their parent principal and open COLLAPSED — the sheet reads as the buy list; expand a parent's + on the left margin to see its children (their £ is apportioned into the parent line). MPN STATUS: engineered TBD 1/61 bought-out lines await detailed design (score penalised by the engineered-TBD fraction — a fully-TBD bill cannot reach 8) · commodity 8/15 small parts carry 'commodity — MPN at procurement' (commodity noun family + unit £ ≤ £100, both required — unpenalised, tallied separately; real practice carries no MPN on class-basis commodity parts at concept stage) · generic-spec 0/0 engine-refused process valves carry 'generic spec — MPN at procurement' (a spec-complete DN/material/rating on the row itself, no £ cap — unpenalised) · OEM-proprietary 2/2 lines carry 'OEM-proprietary (no public MPN)' (a recorded research finding on the row, never self-declared — unpenalised). ROW CHECK CONTRACT (score = 10 × rows-passing ÷ rows − 4 × engineered-TBD-fraction = 10 × 417/417 − 4 × 0.016 = 9.9): MPN TALLIES: resolved 60/61 · engineered TBD 1/61 (penalised) · commodity 'MPN at procurement' 8/15 (unpenalised, visible; noun family + unit £ ≤ £100, both required) · generic spec — MPN at procurement 0/0 (unpenalised, visible; engine-refused process valve with a spec-complete DN/material/rating on its own row, no £ cap) · OEM-proprietary (no public MPN) 2/2 (unpenalised, visible; requires a recorded research finding on the row, never self-declared). Tag/Item=required_nonempty · Class fit=computed · Qty=required_nonempty · Unit £ / Line £=computed · Basis=required_nonempty · Material=computed · MPN / datasheet=computed. A dash / empty / unverifiable contracted cell FAILS its row — honest red beats fake green. | [16 empty] | SG: Very tricky to verify the BOM without the design and quotes for the various parts.
Tag | Item | Qty | Unit £ | Line £ | Cost method | Key inputs | Factors | Est class | Confidence | Duty / rating | Material | Sizing calc (basis) | MPN / datasheet | Row check | Audit: check evidence (build-computed) | Cell check
X-104 | Electrical Control Panel | 1 | 800 | 800 | class_reference | class-reference price (no itemised inputs) | floored; catalogue | 4 | moderate | Electrical Control Panel | N/A — proprietary assembly / bought-out package, see datasheet | catalogue · floored to min credible price | Rittal 1180.000 | PASS |  | PASS
X-107 / X-110 | Circuit Breaker | 2 | 283 | 566 | catalogue | catalogue-class budget (no itemised inputs) | catalogue | 2 | high | Circuit Breakers | N/A — proprietary assembly / bought-out package, see datasheet | catalogue | ABB 1SDA067417R1 | PASS |  | PASS
X-108 / X-111 | Terminal Block | 2 | 1.5 | 3 | catalogue | catalogue-class budget (no itemised inputs) | catalogue | 2 | high | Terminal Blocks | N/A — proprietary assembly / bought-out package, see datasheet | catalogue | WAGO 2002-1301 | PASS |  | PASS
D-101 | 3 Phase Power Input | 1 | 168 | 168 | catalogue | catalogue-class budget (no itemised inputs) | catalogue | 2 | high | 3 Phase Power Input | N/A — proprietary assembly / bought-out package, see datasheet | catalogue | TDK-Lambda DRB240-24-3-A0 | PASS |  | PASS
X-109 | DC Power Cabling | 1 | 3 | 3 | llm_estimate | model estimate (no itemised inputs) | parametric | 5 | low | DC Power Cabling | N/A — proprietary assembly / bought-out package, see datasheet | bottom-up parametric | commodity — MPN at procurement | PASS |  | PASS
G-201 | Standby Diesel Generator · 60 kVA · 862x733x948 mm | 1 | 19200 | 19200 | class_reference | 60 kVA | £320/kVA; install; rating-based | 4 | low | Standby Diesel Generator · 60 kVA · 862x733x948 mm | N/A — proprietary assembly / bought-out package, see datasheet | rating-based: 60 kVA × £320/kVA (UK-2026 installed mid; band £200-440/kVA) — standby diesel genset @ £/kVA [£44,840 above band → grounded to market] | Pramac GBW60P | PASS |  | PASS
U-201 | Control + Instrument UPS · 5 kW (30 min) · 600x510x660 mm | 1 | 4000 | 4000 | class_reference | 5 kVA | £550/kVA; install; rating-based | 4 | moderate | Control + Instrument UPS · 5 kW (30 min) · 600x510x660 mm | N/A — proprietary assembly / bought-out package, see datasheet | rating-based: 5 kVA × £550/kVA (UK-2026 installed mid; band £300-950/kVA) — UPS @ £/kVA [£21,500 above band → grounded to market] | Eaton 9SX5KI | PASS |  | PASS
EP-103 | SCADA / Plant Control System · 53 kW plant | 1 | 62650 | 62650 | class_reference | 53 kW | £50/kW; install; class budget; catalogue | 4 | low | SCADA / Plant Control System · 53 kW plant | N/A — proprietary assembly / bought-out package, see datasheet | installed process system — catalogue-class budget: £60k base (redundant PLC racks + SCADA servers + operator HMIs + I/O + plant network + software licences + panel build + commissioning; supply + install) + £50/kW × ~53 kW connected plant load | Hoogendoorn iSii | PASS |  | PASS
TX-102 | Distribution Transformer · 75 kVA | 1 | 3000 | 3000 | class_reference | 75 kVA | £28/kVA; install; rating-based | 4 | low | Distribution Transformer · 75 kVA | N/A — proprietary assembly / bought-out package, see datasheet | rating-based: 75 kVA × £28/kVA (UK-2026 installed mid; band £15-55/kVA) — transformer @ £/kVA [£18 below band → grounded to market] | Hammond Power Solutions SG3A0075KB | PASS |  | PASS
EP-104 | Motor Control Center | 1 | 3000 | 3000 | llm_estimate | model estimate (no itemised inputs) | floored; catalogue | 5 | low | Motor Control Center | N/A — proprietary assembly / bought-out package, see datasheet | catalogue · floored to min credible price | Eaton Freedom 2100 | PASS |  | PASS
F-1 | Toray HFU-2020AN RO Membrane Elements · 364 m² area | 1 | 9100 | 9100 | class_reference | 364 m² | £25/m²; take-off; parametric | 4 | low | Toray HFU-2020AN RO Membrane Elements · 364 m² area | membrane/filtration media | membrane-area parametric: 364 m² × £25/m² (spiral-wound/UF module supply, UK-2026; NOT a steel take-off) | bespoke fabrication to drawing — see sizing basis | PASS |  | PASS
—.1 | ↳ Pressure Vessel Shell · 15 m³/h | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
—.2 | ↳ Filter Media / Membrane Elements | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
—.3 | ↳ Upper Distribution Header | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
—.4 | ↳ Lower Underdrain / Nozzle Plate | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
—.5 | ↳ Backwash / Service Valve Nest | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
—.6 | ↳ Differential-Pressure Gauges | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
—.7 | ↳ Air Scour / Vent | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
—.8 | ↳ Sample Cock | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
—.9 | ↳ Skid Frame & Pipework | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
—.10 | ↳ Nameplate | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
Z-103 | Ultrafiltration Module | 1 | 14825 | 0 | class_reference |  | parametric | 4 | low |  |  |  |  | FAIL — line ≠ qty×unit, a required cell empty, or qty/£ non-positive |  | PASS
Z-103.1 | ↳ Pressure Vessel Shell · 15 m³/h | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
Z-103.2 | ↳ Filter Media / Membrane Elements | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
Z-103.3 | ↳ Upper Distribution Header | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
Z-103.4 | ↳ Lower Underdrain / Nozzle Plate | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
Z-103.5 | ↳ Backwash / Service Valve Nest | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
Z-103.6 | ↳ Differential-Pressure Gauges | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
Z-103.7 | ↳ Air Scour / Vent | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
Z-103.8 | ↳ Sample Cock | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
Z-103.9 | ↳ Skid Frame & Pipework | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
Z-103.10 | ↳ Nameplate | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
X-112 | Hydraulic Connectors | 1 | 1 | 1 | llm_estimate | model estimate (no itemised inputs) | parametric | 5 | low | Hydraulic Connectors | N/A — proprietary assembly / bought-out package, see datasheet | bottom-up parametric | commodity — MPN at procurement | PASS |  | PASS
V-102 | Uv Disinfection · 4 kW · 600x510x660 mm | 1 | 17540 | 17540 | class_reference | median £34,360, n=5 | 35%; £12,012→£17,540; lifted; corpus; catalogue | 4 | low | Uv Disinfection · 4 kW · 600x510x660 mm | PVC-U / 304 stainless (WRAS) | catalogue · MoC: PVC-U / 304 stainless (WRAS) for potable-water service (WRAS-approved wetted materials) · lifted £12,012→£17,540 to the engine corpus p25 (median £34,360, n=5; line was 35% of median — under-priced vs the engine's own forge-truth reference) | WEDECO (Xylem) Spektron 30e | PASS |  | PASS
V-102.1 | ↳ Process Unit | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
V-102.2 | ↳ Inlet / Outlet Manifolds | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
V-102.3 | ↳ Flow Control Valve | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
V-102.4 | ↳ Dosing / Lamp Module | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | moderate |  |  |  |  | PASS |  | PASS
V-102.5 | ↳ Local Sensor | 1 | incl. in parent | — | class_reference |  | catalogue | 4 | low |  |  |  |  | PASS |  | PASS
V-102.6 | ↳ Control & Power Module | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
V-102.7 | ↳ Mounting Frame | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
V-106 | Softener Vessel · 1.2 m dia x 1.3 m | 2 | 8000 | 16000 | class_reference | 5 mm; 1.3 m; 13 kPa; 120 MPa; 6 m²; 259 kg; median £12,581 | ×1.3; × 259; £4.5/kg; × 1.25; 28%; £3,548→£8,000; lifted; | 4 | low | Softener Vessel · 1.2 m dia x 1.3 m | carbon steel | tapered wall 5 mm = P·r/(σ·E)+c · ⌀1.2×1.3 m (open top (no head)) · P=13 kPa head · σ=120 MPa → 6 m² × 259 kg carbon steel @ £4.5/kg supply × 1.25 erection + fittings · named part Pentair Structural '36X72 COMP 6"TF 6"BF' rejected: Engine B priced it £840 via its small-parts commodity curve — no catalogue class exists for a bespoke fabricated tank/vessel shell; a materials take-off is used instead · lifted £3,548→£8,000 to the engine corpus p25 (median £12,581, n=5; line was 28% of median — under-priced vs the engine's own forge-truth reference) | Pentair Structural 36X72 COMP 6"TF 6"BF | PASS |  | PASS
V-106.1 | ↳ Shell Course | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
V-106.2 | ↳ Top Head / Roof | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
V-106.3 | ↳ Base / Floor Plate | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
V-106.4 | ↳ Support Skirt / Legs | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
V-106.5 | ↳ Manway & Cover | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
V-106.6 | ↳ Inlet Nozzle Set | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
V-106.7 | ↳ Outlet Nozzle Set | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
V-106.8 | ↳ Drain Nozzle | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
V-106.9 | ↳ Overflow / Weir | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
V-106.10 | ↳ Internal Distribution | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
V-106.11 | ↳ Tank Vent / Pressure Relief | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
V-106.12 | ↳ Access Ladder & Platform | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
V-106.13 | ↳ Internal Lining / Coating | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
V-106.14 | ↳ Earthing Boss | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
V-106.15 | ↳ Nameplate | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
P-106 | Fertigation Dosing Pump · 8 kW · 600x510x660 mm | 2 | 8634 | 17268 | class_reference | class-reference price (no itemised inputs) | catalogue | 4 | low | Fertigation Dosing Pump · 8 kW · 600x510x660 mm | PVC-U / 304 stainless (WRAS) | catalogue · MoC: PVC-U / 304 stainless (WRAS) for potable-water service (WRAS-approved wetted materials) | Grundfos 96122012 | PASS |  | PASS
P-106.1 | ↳ Casing | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
P-106.2 | ↳ Impeller / Rotor | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
P-106.3 | ↳ Drive Motor · 7.5 kW | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
P-106.4 | ↳ Variable-Speed Drive · 7.5 kW | 1 | incl. in parent | — | catalogue |  | catalogue; parametric | 2 | high |  |  |  |  | PASS |  | PASS
P-106.5 | ↳ Flexible Coupling | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
P-106.6 | ↳ Coupling Guard | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
P-106.7 | ↳ Baseplate | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
P-106.8 | ↳ Mechanical Seal | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
P-106.9 | ↳ Suction Isolation Valve (on Fertigation Dosing Pump) | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
P-106.10 | ↳ Discharge Isolation Valve (on Fertigation Dosing Pump) | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
P-106.11 | ↳ Non-Return Valve (on Fertigation Dosing Pump) | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
P-106.12 | ↳ Discharge Pressure Gauge | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
P-106.13 | ↳ Anti-Vibration Mounts | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
TK-103 | Nutrient Tank · 1.1 m dia x 1.1 m | 8 | 2844 | 22752 | class_reference | 6 mm; 1.1 m; 11 kPa; 18 MPa; 5 m²; 58 kg | ×1.1; × 58; £12.0/kg; × 1.25 | 4 | low | Nutrient Tank · 1.1 m dia x 1.1 m | FRP/GRP | tapered wall 6 mm = P·r/(σ·E)+c · ⌀1.1×1.1 m (open top (no head)) · P=11 kPa head · σ=18 MPa → 5 m² × 58 kg FRP/GRP @ £12.0/kg supply × 1.25 erection + fittings | bespoke fabrication to drawing — see sizing basis | PASS |  | PASS
TK-103.1 | ↳ Tank Wall (laminate) | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
TK-103.2 | ↳ Tank Floor (graded to centre) | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
TK-103.3 | ↳ Dual Drain / Centre Standpipe | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
TK-103.4 | ↳ Side Drain & Overflow | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
TK-103.5 | ↳ Inlet Distribution Ring | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
TK-103.6 | ↳ Internal Flow Baffles | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
TK-103.7 | ↳ Rim Stiffener | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
TK-103.8 | ↳ Access Walkway & Handrail | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
TK-103.9 | ↳ Internal Gelcoat / Lining | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
TK-103.10 | ↳ Earthing Boss | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
TK-103.11 | ↳ Nameplate | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
P-102 | Hand Watering Pump · 25 m³/h · 900x500x700 mm | 1 | 2500 | 2500 | class_reference | 3 kW | £700/kW; install; rating-based | 4 | low | Hand Watering Pump · 25 m³/h · 900x500x700 mm | PVC-U / 304 stainless (WRAS) | rating-based: 3 kW × £700/kW (UK-2026 installed mid; band £350-1300/kW) — process pump (skid: casing+motor+VSD) @ £/kW [£8,110 above band → grounded to market] · motor kW from contract hand_watering_pump_motor_kw (the line's own rating is a flow, not a power) · MoC: PVC-U / 304 stainless (WRAS) for potable-water service (WRAS-approved wetted materials) | Grundfos 96935501 | PASS |  | PASS
P-102.1 | ↳ Casing | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
P-102.2 | ↳ Impeller / Rotor | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
P-102.3 | ↳ Drive Motor · 3 kW | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
P-102.4 | ↳ Variable-Speed Drive · 3 kW | 1 | incl. in parent | — | catalogue | incl. in parent line |  | 2 | high |  |  |  |  | PASS |  | PASS
P-102.5 | ↳ Flexible Coupling | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
P-102.6 | ↳ Coupling Guard | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
P-102.7 | ↳ Baseplate | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
P-102.8 | ↳ Mechanical Seal | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
P-102.9 | ↳ Suction Isolation Valve (on Hand Watering Pump) (on Hand Watering Pump) | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
P-102.10 | ↳ Discharge Isolation Valve (on Hand Watering Pump) (on Hand Watering Pump) | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
P-102.11 | ↳ Non-Return Valve (on Hand Watering Pump) (on Hand Watering Pump) | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
P-102.12 | ↳ Discharge Pressure Gauge | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
P-102.13 | ↳ Anti-Vibration Mounts | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
TK-114 | Drain Collection Sump · 2.1 m dia x 1.4 m | 2 | 4683 | 9366 | class_reference | 6 mm; 1.4 m; 14 kPa; 18 MPa; 13 m²; 160 kg | ×1.4; × 160; £12.0/kg; × 1.25 | 4 | low | Drain Collection Sump · 2.1 m dia x 1.4 m | FRP/GRP | tapered wall 6 mm = P·r/(σ·E)+c · ⌀2.1×1.4 m (open top (no head)) · P=14 kPa head · σ=18 MPa → 13 m² × 160 kg FRP/GRP @ £12.0/kg supply × 1.25 erection + fittings | bespoke fabrication to drawing — see sizing basis | PASS |  | PASS
TK-114.1 | ↳ Tank Wall (laminate) | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
TK-114.2 | ↳ Tank Floor (graded to centre) | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
TK-114.3 | ↳ Dual Drain / Centre Standpipe | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
TK-114.4 | ↳ Side Drain & Overflow | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
TK-114.5 | ↳ Inlet Distribution Ring | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
TK-114.6 | ↳ Internal Flow Baffles | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
TK-114.7 | ↳ Rim Stiffener | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
TK-114.8 | ↳ Access Walkway & Handrail | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
TK-114.9 | ↳ Internal Gelcoat / Lining | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
TK-114.10 | ↳ Earthing Boss | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
TK-114.11 | ↳ Nameplate | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
P-104 | Drain Transfer Pump · 2 kW · 600x510x660 mm | 2 | 1850 | 3700 | class_reference | 2kw |  | 4 | low | Drain Transfer Pump · 2 kW · 600x510x660 mm | PVC-U / 304 stainless (WRAS) | real DB median of 1 comparable 2kw 'pump' parts (forge-truth.db) · MoC: PVC-U / 304 stainless (WRAS) for potable-water service (WRAS-approved wetted materials) | Grundfos SL1.50.65.22.2.50D.C | PASS |  | PASS
P-104.1 | ↳ Casing | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
P-104.2 | ↳ Impeller / Rotor | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
P-104.3 | ↳ Drive Motor · 2.2 kW | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
P-104.4 | ↳ Variable-Speed Drive · 2.2 kW | 1 | incl. in parent | — | catalogue |  | catalogue; parametric | 2 | high |  |  |  |  | PASS |  | PASS
P-104.5 | ↳ Flexible Coupling | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
P-104.6 | ↳ Coupling Guard | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
P-104.7 | ↳ Baseplate | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
P-104.8 | ↳ Mechanical Seal | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
P-104.9 | ↳ Suction Isolation Valve (on Drain Transfer Pump) (on Drain Transfer Pump) | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
P-104.10 | ↳ Discharge Isolation Valve (on Drain Transfer Pump) (on Drain Transfer Pump) | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
P-104.11 | ↳ Non-Return Valve (on Drain Transfer Pump) (on Drain Transfer Pump) | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
P-104.12 | ↳ Discharge Pressure Gauge | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
P-104.13 | ↳ Anti-Vibration Mounts | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
V-104 | Cloth Filter · 80 m³/h · 3 m² area | 2 | 8270 | 16540 | llm_estimate | 3 m²; 0 bar | £90/m²; take-off | 5 | low | Cloth Filter · 80 m³/h · 3 m² area | structural steel | structural steelwork take-off: 3 m² plan × £90/m² (UK-2026 fabricated + erected; service=structural, dry, 0 bar — NOT a pressure shell) + £8k connections | bespoke fabrication to drawing — see sizing basis | PASS |  | PASS
V-104.1 | ↳ Drum / Element · 80 m³/h | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
V-104.2 | ↳ Media / Mesh Panels | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
V-104.3 | ↳ Drive Gearmotor · 1 kW | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
V-104.4 | ↳ Backwash Spray Bar | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
V-104.5 | ↳ Backwash Pump | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
V-104.6 | ↳ Reject Trough | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
V-104.7 | ↳ Differential-Pressure Switch | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | moderate |  |  |  |  | PASS |  | PASS
V-104.8 | ↳ Support Frame | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
V-104.9 | ↳ Local Control Panel | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | moderate |  |  |  |  | PASS |  | PASS
V-103 | Gac Softener · 15 m³/h · 0.9 m dia x 1.8 m | 1 | 14825 | 14825 | class_reference | class-reference price (no itemised inputs) | catalogue | 4 | moderate | Gac Softener · 15 m³/h · 0.9 m dia x 1.8 m | N/A — proprietary assembly / bought-out package, see datasheet | catalogue | Pentair Structural 36X72 COMP 6"TF 6"BF | PASS |  | PASS
V-103.1 | ↳ Pressure Vessel Shell · 15 m³/h | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
V-103.2 | ↳ Filter Media / Membrane Elements | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
V-103.3 | ↳ Upper Distribution Header | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
V-103.4 | ↳ Lower Underdrain / Nozzle Plate | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
V-103.5 | ↳ Backwash / Service Valve Nest | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
V-103.6 | ↳ Differential-Pressure Gauges | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
V-103.7 | ↳ Air Scour / Vent | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
V-103.8 | ↳ Sample Cock | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
V-103.9 | ↳ Skid Frame & Pipework | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
V-103.10 | ↳ Nameplate | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
P-103 | Irrigation Pump · 90 m³/h · 1379x766x1073 mm | 1 | 9413 | 9413 | class_reference | 45 m³ | × 2; catalogue | 4 | low | Irrigation Pump · 90 m³/h · 1379x766x1073 mm | PVC-U / 304 stainless (WRAS) | catalogue · MoC: PVC-U / 304 stainless (WRAS) for potable-water service (WRAS-approved wetted materials) · demand-sized: peak irrigation demand = 45 m³/h per department × 2 departments | Grundfos 96539165 | PASS |  | PASS
P-103.1 | ↳ Casing | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
P-103.2 | ↳ Impeller / Rotor | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
P-103.3 | ↳ Drive Motor · 11 kW | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
P-103.4 | ↳ Variable-Speed Drive · 11 kW | 1 | incl. in parent | — | catalogue | incl. in parent line |  | 2 | high |  |  |  |  | PASS |  | PASS
P-103.5 | ↳ Flexible Coupling | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
P-103.6 | ↳ Coupling Guard | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
P-103.7 | ↳ Baseplate | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
P-103.8 | ↳ Mechanical Seal | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
P-103.9 | ↳ Suction Isolation Valve (on Irrigation Pump) (on Irrigation Pump) | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
P-103.10 | ↳ Discharge Isolation Valve (on Irrigation Pump) (on Irrigation Pump) | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
P-103.11 | ↳ Non-Return Valve (on Irrigation Pump) (on Irrigation Pump) | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
P-103.12 | ↳ Discharge Pressure Gauge | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
P-103.13 | ↳ Anti-Vibration Mounts | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
M-101 | Distribution Manifold · 45 m³/h · 700x595x770 mm | 2 | 1725 | 3450 | class_reference | 45 m³ | parametric | 4 | low | Distribution Manifold · 45 m³/h · 700x595x770 mm | PVC-U / 304 stainless (WRAS) | distribution-manifold parametric: 45 m³/h delivery duty × £25/(m³·h) + £600 base — fabricated header + isolation/non-return valves + gauge tappings + supports (supply-only materials; field labour in the cost stack) · MoC: PVC-U / 304 stainless (WRAS) for potable-water service (WRAS-approved wetted materials) | bespoke fabrication to drawing — see sizing basis | PASS |  | PASS
Z-101 | Reverse Osmosis Skid · 2.3 m dia x 2.4 m | 1 | 8737 | 8737 | class_reference | 8 m²; 0 bar | £90/m²; take-off | 4 | low | Reverse Osmosis Skid · 2.3 m dia x 2.4 m | structural steel | structural steelwork take-off: 8 m² plan × £90/m² (UK-2026 fabricated + erected; service=structural, dry, 0 bar — NOT a pressure shell) + £8k connections | bespoke fabrication to drawing — see sizing basis | PASS |  | PASS
Z-101.1 | ↳ Pressure Vessel Shell · 15 m³/h | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
Z-101.2 | ↳ Filter Media / Membrane Elements | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
Z-101.3 | ↳ Upper Distribution Header | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
Z-101.4 | ↳ Lower Underdrain / Nozzle Plate | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
Z-101.5 | ↳ Backwash / Service Valve Nest | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
Z-101.6 | ↳ Differential-Pressure Gauges | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
Z-101.7 | ↳ Air Scour / Vent | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
Z-101.8 | ↳ Sample Cock | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
Z-101.9 | ↳ Skid Frame & Pipework | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
Z-101.10 | ↳ Nameplate | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
P-101 | Ro High Pressure Pump · 4 kW · 600x510x660 mm | 1 | 3850 | 3850 | class_reference | 4kw |  | 4 | low | Ro High Pressure Pump · 4 kW · 600x510x660 mm | PVC-U / 304 stainless (WRAS) | real DB median of 1 comparable 4kw 'pump' parts (forge-truth.db) · MoC: PVC-U / 304 stainless (WRAS) for potable-water service (WRAS-approved wetted materials) | Grundfos 96502039 | PASS |  | PASS
P-101.1 | ↳ Casing | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
P-101.2 | ↳ Impeller / Rotor | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
P-101.3 | ↳ Drive Motor · 4.2 kW | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
P-101.4 | ↳ Variable-Speed Drive · 4.2 kW | 1 | incl. in parent | — | catalogue | incl. in parent line |  | 2 | high |  |  |  |  | PASS |  | PASS
P-101.5 | ↳ Flexible Coupling | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
P-101.6 | ↳ Coupling Guard | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
P-101.7 | ↳ Baseplate | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
P-101.8 | ↳ Mechanical Seal | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
P-101.9 | ↳ Suction Isolation Valve (on Ro High Pressure Pump) | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
P-101.10 | ↳ Discharge Isolation Valve (on Ro High Pressure Pump) | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
P-101.11 | ↳ Non-Return Valve (on Ro High Pressure Pump) | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
P-101.12 | ↳ Discharge Pressure Gauge | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
P-101.13 | ↳ Anti-Vibration Mounts | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
V-101 | Gac Filter · 1.3 m dia x 1.4 m | 1 | 18 | 18 | class_reference | median £18, n=5 | 22%; £4→£18; lifted; corpus; catalogue | 4 | low | Gac Filter · 1.3 m dia x 1.4 m | PVC-U / 304 stainless (WRAS) | catalogue · MoC: PVC-U / 304 stainless (WRAS) for potable-water service (WRAS-approved wetted materials) · lifted £4→£18 to the engine corpus 0.6×median (median £18, n=5; line was 22% of median — under-priced vs the engine's own forge-truth reference) | General Carbon HP-1000 | PASS |  | PASS
V-101.1 | ↳ Pressure Vessel Shell · 15 m³/h | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
V-101.2 | ↳ Filter Media / Membrane Elements | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
V-101.3 | ↳ Upper Distribution Header | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
V-101.4 | ↳ Lower Underdrain / Nozzle Plate | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
V-101.5 | ↳ Backwash / Service Valve Nest | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
V-101.6 | ↳ Differential-Pressure Gauges | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
V-101.7 | ↳ Air Scour / Vent | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
V-101.8 | ↳ Sample Cock | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
V-101.9 | ↳ Skid Frame & Pipework | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
V-101.10 | ↳ Nameplate | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
TK-108 | Fresh Water Tank · 3.7 m dia x 3.7 m | 1 | 13615 | 13615 | class_reference | 6 mm; 3.7 m; 36 kPa; 18 MPa; 54 m²; 656 kg | ×3.7; × 656; £12.0/kg; × 1.25 | 4 | low | Fresh Water Tank · 3.7 m dia x 3.7 m | FRP/GRP | tapered wall 6 mm = P·r/(σ·E)+c · ⌀3.7×3.7 m (open top (no head)) · P=36 kPa head · σ=18 MPa → 54 m² × 656 kg FRP/GRP @ £12.0/kg supply × 1.25 erection + fittings | bespoke fabrication to drawing — see sizing basis | PASS |  | PASS
TK-108.1 | ↳ Tank Wall (laminate) | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
TK-108.2 | ↳ Tank Floor (graded to centre) | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
TK-108.3 | ↳ Dual Drain / Centre Standpipe | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
TK-108.4 | ↳ Side Drain & Overflow | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
TK-108.5 | ↳ Inlet Distribution Ring | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
TK-108.6 | ↳ Internal Flow Baffles | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
TK-108.7 | ↳ Rim Stiffener | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
TK-108.8 | ↳ Access Walkway & Handrail | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
TK-108.9 | ↳ Internal Gelcoat / Lining | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
TK-108.10 | ↳ Earthing Boss | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
TK-108.11 | ↳ Nameplate | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
TK-106 | Drain Water Tank · 3.7 m dia x 3.7 m | 2 | 13615 | 27230 | class_reference | 6 mm; 3.7 m; 36 kPa; 18 MPa; 54 m²; 656 kg | ×3.7; × 656; £12.0/kg; × 1.25 | 4 | low | Drain Water Tank · 3.7 m dia x 3.7 m | FRP/GRP | tapered wall 6 mm = P·r/(σ·E)+c · ⌀3.7×3.7 m (open top (no head)) · P=36 kPa head · σ=18 MPa → 54 m² × 656 kg FRP/GRP @ £12.0/kg supply × 1.25 erection + fittings | bespoke fabrication to drawing — see sizing basis | PASS |  | PASS
TK-106.1 | ↳ Tank Wall (laminate) | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
TK-106.2 | ↳ Tank Floor (graded to centre) | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
TK-106.3 | ↳ Dual Drain / Centre Standpipe | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
TK-106.4 | ↳ Side Drain & Overflow | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
TK-106.5 | ↳ Inlet Distribution Ring | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
TK-106.6 | ↳ Internal Flow Baffles | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
TK-106.7 | ↳ Rim Stiffener | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
TK-106.8 | ↳ Access Walkway & Handrail | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
TK-106.9 | ↳ Internal Gelcoat / Lining | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
TK-106.10 | ↳ Earthing Boss | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
TK-106.11 | ↳ Nameplate | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
X-113 | Compartment Spacers | 1 | 3 | 3 | class_reference | class-reference price (no itemised inputs) | parametric | 4 | moderate | Compartment Spacers | N/A — proprietary assembly / bought-out package, see datasheet | bottom-up parametric · commodity-floor (estimate £0.11 renders £0; 'spacers' → £3) | commodity — MPN at procurement | PASS |  | PASS
F-2 | Uf Membrane Bank · 364 m² area | 1 | 9100 | 9100 | class_reference | 364 m² | £25/m²; take-off; parametric | 4 | low | Uf Membrane Bank · 364 m² area | membrane/filtration media | membrane-area parametric: 364 m² × £25/m² (spiral-wound/UF module supply, UK-2026; NOT a steel take-off) · merged synonym line(s): 'Ultrafiltration Module' (was £14,825), 'Uf Module Bank' (was £14,825) | bespoke fabrication to drawing — see sizing basis | PASS |  | PASS
—.1 | ↳ Pressure Vessel Shell · 15 m³/h | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
—.2 | ↳ Filter Media / Membrane Elements | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
—.3 | ↳ Upper Distribution Header | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
—.4 | ↳ Lower Underdrain / Nozzle Plate | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
—.5 | ↳ Backwash / Service Valve Nest | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
—.6 | ↳ Differential-Pressure Gauges | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
—.7 | ↳ Air Scour / Vent | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
—.8 | ↳ Sample Cock | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
—.9 | ↳ Skid Frame & Pipework | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
—.10 | ↳ Nameplate | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
Z-102 | Uf Module Bank | 1 | 14825 | 0 | class_reference |  | take-off | 4 | low |  |  |  |  | FAIL — line ≠ qty×unit, a required cell empty, or qty/£ non-positive |  | PASS
Z-102.1 | ↳ Pressure Vessel Shell · 15 m³/h | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
Z-102.2 | ↳ Filter Media / Membrane Elements | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
Z-102.3 | ↳ Upper Distribution Header | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
Z-102.4 | ↳ Lower Underdrain / Nozzle Plate | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
Z-102.5 | ↳ Backwash / Service Valve Nest | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
Z-102.6 | ↳ Differential-Pressure Gauges | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
Z-102.7 | ↳ Air Scour / Vent | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
Z-102.8 | ↳ Sample Cock | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
Z-102.9 | ↳ Skid Frame & Pipework | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
Z-102.10 | ↳ Nameplate | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
X-114 / X-121 | PLC Controller | 2 | 160 | 320 | catalogue | catalogue-class budget (no itemised inputs) | catalogue | 2 | high | PLC Controller | N/A — proprietary assembly / bought-out package, see datasheet | catalogue | Siemens 6ES7241-1CH32-0XB0 | PASS |  | PASS
X-115 | Veolia Ro40 Controller | 1 | 12 | 12 | llm_estimate | model estimate (no itemised inputs) | catalogue; parametric | 5 | low | Veolia Ro40 Controller | N/A — proprietary assembly / bought-out package, see datasheet | bottom-up parametric · OEM-proprietary — no public MPN (verified 2026-07-04: Veolia Water Technologies RO40 (Ionpro RO skid controller line) datasheets + distributor catalogues checked — no publicly listed part/model number found) | OEM-proprietary (no public MPN) | PASS |  | PASS
X-116 / X-122 | Modbus Interface | 2 | 270 | 540 | catalogue | catalogue-class budget (no itemised inputs) | catalogue | 2 | high | Modbus Interface | N/A — proprietary assembly / bought-out package, see datasheet | catalogue | Siemens 6ES7241-1CH32-0XB0 | PASS |  | PASS
X-117 | Ethernet Ip Module | 1 | 330 | 330 | llm_estimate | model estimate (no itemised inputs) | catalogue | 5 | low | Ethernet Ip Module | N/A — proprietary assembly / bought-out package, see datasheet | catalogue | HMS Networks AB7072-B | PASS |  | PASS
X-118 | Hoogendoorn iSii Remote Monitoring | 1 | 982 | 982 | class_reference | median £982, n=5 | 29%; £280→£982; lifted; corpus; catalogue | 4 | low | Hoogendoorn iSii Remote Monitoring | N/A — proprietary assembly / bought-out package, see datasheet | catalogue · lifted £280→£982 to the engine corpus 0.6×median (median £982, n=5; line was 29% of median — under-priced vs the engine's own forge-truth reference) | HMS Networks (Ewon) FLEXY20500_00MA | PASS |  | PASS
X-119 | Dc3 Power Controller | 1 | 12 | 12 | class_reference | class-reference price (no itemised inputs) | catalogue; parametric | 4 | low | Dc3 Power Controller | N/A — proprietary assembly / bought-out package, see datasheet | bottom-up parametric · OEM-proprietary — no public MPN (verified 2026-07-04: Veolia Water Technologies DC3 (Terion dosing/power controller line) datasheets + distributor catalogues checked — no publicly listed part/model number found) | OEM-proprietary (no public MPN) | PASS |  | PASS
X-120 | HMI Touchscreen | 1 | 589 | 589 | catalogue | catalogue-class budget (no itemised inputs) | catalogue | 2 | high | HMI Touchscreen | PVC-U / 304 stainless (WRAS) | catalogue · MoC: PVC-U / 304 stainless (WRAS) for potable-water service (WRAS-approved wetted materials) | Panasonic Industrial Automation AWHS1R070 | PASS |  | PASS
X-123 | Remote Monitoring Gateway | 1 | 280 | 280 | class_reference | class-reference price (no itemised inputs) | catalogue | 4 | low | Remote Monitoring Gateway | N/A — proprietary assembly / bought-out package, see datasheet | catalogue | HMS Networks (Ewon) FLEXY20500_00MA | PASS |  | PASS
I-103 | Digital Control Panel | 1 | 850 | 850 | catalogue | catalogue-class budget (no itemised inputs) | catalogue | 4 | moderate | Digital Control Panel | N/A — proprietary assembly / bought-out package, see datasheet | catalogue | Siemens 6AV2123-2GB03-0AX0 | PASS |  | PASS
X-124 / V-107 | Solenoid Valve | 2 | 393 | 786 | catalogue | catalogue-class budget (no itemised inputs) | catalogue | 2 | high | Solenoid Valves | PVC-U / 304 stainless (WRAS) | catalogue · MoC: PVC-U / 304 stainless (WRAS) for potable-water service (WRAS-approved wetted materials) | Sensata Technologies, Inc. SOL7A4 | PASS |  | PASS
X-125 | Pneumatic Actuated Valves | 200 | 200 | 40000 | class_reference | class-reference price (no itemised inputs) | £1.85/DN·mm | 4 | low | Pneumatic Actuated Valves | PVC-U / 304 stainless (WRAS) | actuated-valve assembly (actuator + valve body as ONE unit): £80 base + £1.85/DN·mm × DN65 assumed (2½ in class) = £200 (UK-2026 trade supply, never the bare-valve band) · MoC: PVC-U / 304 stainless (WRAS) for potable-water service (WRAS-approved wetted materials) | Bürkert Type 2000 | PASS |  | PASS
X-126 | Flow Control Valves | 1 | 18 | 18 | class_reference | class-reference price (no itemised inputs) | catalogue | 4 | low | Flow Control Valves | PVC-U / 304 stainless (WRAS) | catalogue · MoC: PVC-U / 304 stainless (WRAS) for potable-water service (WRAS-approved wetted materials) | Pentair Fleck 2900S | PASS |  | PASS
FCV-201–202 | Inlet Flow Control Valve · 45 m³/h · DN100 modulating control valve (45 m³/h @ 2 m/s) | 2 | 3312 | 6624 | llm_estimate | model estimate (no itemised inputs) | install; class budget; catalogue | 5 | low | Inlet Flow Control Valve · 45 m³/h · DN100 modulating control valve (45 m³/h @ 2 m/s) | N/A — proprietary assembly / bought-out package, see datasheet | installed actuator — catalogue-class budget | Pentair Fleck 2900S | PASS |  | PASS
V-108 | Pneumatic Control Valve | 1 | 200 | 200 | class_reference | class-reference price (no itemised inputs) | £1.85/DN·mm | 4 | low | Pneumatic Control Valve | PVC-U / 304 stainless (WRAS) | actuated-valve assembly (actuator + valve body as ONE unit): £80 base + £1.85/DN·mm × DN65 assumed (2½ in class) = £200 (UK-2026 trade supply, never the bare-valve band) · MoC: PVC-U / 304 stainless (WRAS) for potable-water service (WRAS-approved wetted materials) | Bürkert Type 2301 | PASS |  | PASS
I-104 | Conductivity Sensor | 1 | 12 | 12 | class_reference | class-reference price (no itemised inputs) | catalogue | 4 | low | Conductivity Sensor | N/A — proprietary assembly / bought-out package, see datasheet | catalogue | Myron L 750-II-CS51 | PASS |  | PASS
I-105 / X-127 | Flow Meter | 2 | 691 | 1382 | catalogue | catalogue-class budget (no itemised inputs) | catalogue | 2 | high | Flow Meter | N/A — proprietary assembly / bought-out package, see datasheet | catalogue | Endress+Hauser DMA50-AAABA1 | PASS |  | PASS
I-106 | Ph Sensor | 1 | 12 | 12 | class_reference | class-reference price (no itemised inputs) | catalogue | 4 | low | Ph Sensor | N/A — proprietary assembly / bought-out package, see datasheet | catalogue | Endress+Hauser CPS11E | PASS |  | PASS
I-107 | Orp Sensor | 1 | 12 | 12 | class_reference | class-reference price (no itemised inputs) | catalogue | 4 | low | Orp Sensor | N/A — proprietary assembly / bought-out package, see datasheet | catalogue | Endress+Hauser CPS12D | PASS |  | PASS
LT-201–213 | Level Transmitter · 0–1.4 m | 13 | 1843 | 23959 | llm_estimate | 1.4 m; median £2,800, n=5 | ×2; ×8; ×1; 32%; £900→£1,843; lifted; corpus; install; cla | 5 | low | Level Transmitter · 0–1.4 m | N/A — proprietary assembly / bought-out package, see datasheet | installed instrument — catalogue-class budget · qty 13 = one per monitored vessel (a contract-declared control variable is measured on EVERY vessel that holds it — stated engineering rule); locations: softener vessel ×2 (0–1.4 m), nutrient tank ×8 (0–1.4 m), drain collection sump ×2 (0–1.4 m), gac filter ×1 (0–1.4 m) · lifted £900→£1,843 to the engine corpus p25 (median £2,800, n=5; line was 32% of median — under-priced vs the engine's own forge-truth reference) | Endress+Hauser Waterpilot FMX21 | PASS |  | PASS
LT-214 | Level Transmitter · 0–3 m | 1 | 1843 | 1843 | llm_estimate | median £2,800, n=5 | 32%; £900→£1,843; lifted; corpus; install; class budget; c | 5 | low | Level Transmitter · 0–3 m | N/A — proprietary assembly / bought-out package, see datasheet | installed instrument — catalogue-class budget · lifted £900→£1,843 to the engine corpus p25 (median £2,800, n=5; line was 32% of median — under-priced vs the engine's own forge-truth reference) | Endress+Hauser Waterpilot FMX21 | PASS |  | PASS
LT-215–217 | Level Transmitter · 0–4 m | 3 | 1843 | 5529 | llm_estimate | 4 m; median £2,800, n=5 | ×1; ×2; 32%; £900→£1,843; lifted; corpus; install; class b | 5 | low | Level Transmitter · 0–4 m | N/A — proprietary assembly / bought-out package, see datasheet | installed instrument — catalogue-class budget · qty 3 = one per monitored vessel (a contract-declared control variable is measured on EVERY vessel that holds it — stated engineering rule); locations: fresh water tank ×1 (0–4 m), drain water tank ×2 (0–4 m) · lifted £900→£1,843 to the engine corpus p25 (median £2,800, n=5; line was 32% of median — under-priced vs the engine's own forge-truth reference) | Endress+Hauser Waterpilot FMX21 | PASS |  | PASS
AT-201 | pH Analyser · pH 0–14 (control 0.3) | 1 | 2800 | 2800 | llm_estimate | median £2,800, n=5 | 46%; £1,300→£2,800; lifted; corpus; install; class budget; | 5 | low | pH Analyser · pH 0–14 (control 0.3) | N/A — proprietary assembly / bought-out package, see datasheet | installed instrument — catalogue-class budget · lifted £1,300→£2,800 to the engine corpus 0.6×median (median £2,800, n=5; line was 46% of median — under-priced vs the engine's own forge-truth reference) | Hach LXV404.99.05112 | PASS |  | PASS
PT-201–217 | Pressure Transmitter · 0–5 bar | 17 | 700 | 11900 | catalogue | 5 bar | ×2; ×8; ×1; install; class budget; catalogue | 2 | high | Pressure Transmitter · 0–5 bar | N/A — proprietary assembly / bought-out package, see datasheet | installed instrument — catalogue-class budget · qty 17 = one per monitored vessel (a contract-declared control variable is measured on EVERY vessel that holds it — stated engineering rule); locations: softener vessel ×2 (0–5 bar), nutrient tank ×8 (0–5 bar), drain collection sump ×2 (0–5 bar), reverse osmosis skid ×1 (0–5 bar), gac filter ×1 (0–5 bar), fresh water tank ×1 (0–5 b | Telemecanique XMLP150PD130 | PASS |  | PASS
I-108 | Silica Analyzer | 1 | 280 | 280 | llm_estimate | model estimate (no itemised inputs) | catalogue | 5 | low | Silica Analyzer | N/A — proprietary assembly / bought-out package, see datasheet | catalogue | Hach 5500sc | PASS |  | PASS
I-109 | Chlorine Sensor | 1 | 12 | 12 | class_reference | class-reference price (no itemised inputs) | catalogue | 4 | low | Chlorine Sensor | N/A — proprietary assembly / bought-out package, see datasheet | catalogue | Hach LXV45B.99.11022 | PASS |  | PASS
I-110 | Tds Sensor | 1 | 12 | 12 | class_reference | class-reference price (no itemised inputs) | catalogue | 4 | low | Tds Sensor | N/A — proprietary assembly / bought-out package, see datasheet | catalogue | Myron L 750-II-CS51 | PASS |  | PASS
EP-102 | Mains Incomer · 125 A · 400 V 3-phase LV incomer · 125 A ACB frame (sized to 53 kW connected load, PF 0.9, 25% margin) | 1 | 283 | 283 | catalogue | catalogue-class budget (no itemised inputs) | catalogue | 4 | moderate | Mains Incomer · 125 A · 400 V 3-phase LV incomer · 125 A ACB frame (sized to 53 kW connected load, PF 0.9, 25% margin) | N/A — proprietary assembly / bought-out package, see datasheet | catalogue | ABB 1SDA067417R1 | PASS |  | PASS
EP-101 | Main Switchboard · 125 A · 400 V 3-phase LV incomer · 125 A ACB frame (sized to 53 kW connected load, PF 0.9, 25% margin) | 1 | 4250 | 4250 | class_reference | class-reference price (no itemised inputs) | catalogue | 4 | low | Main Switchboard · 125 A · 400 V 3-phase LV incomer · 125 A ACB frame (sized to 53 kW connected load, PF 0.9, 25% margin) | N/A — proprietary assembly / bought-out package, see datasheet | catalogue | Schneider Electric BlokSeT MB301M | PASS |  | PASS
X-128 | Power Supply Unit | 1 | 219 | 219 | catalogue | catalogue-class budget (no itemised inputs) | catalogue | 2 | high | Power Supply Unit | N/A — proprietary assembly / bought-out package, see datasheet | catalogue | Omron Automation and Safety S8VS-09024BP | PASS |  | PASS
X-129 | Surge Protection Device | 1 | 250 | 250 | llm_estimate | model estimate (no itemised inputs) | catalogue | 5 | low | Surge Protection Device | N/A — proprietary assembly / bought-out package, see datasheet | catalogue | Phoenix Contact 2838199 | PASS |  | PASS
X-106 | Permeate Outlet | 1 | 9 | 9 | llm_estimate | model estimate (no itemised inputs) | parametric | 5 | low | Permeate Outlet | N/A — proprietary assembly / bought-out package, see datasheet | bottom-up parametric | commodity — MPN at procurement | PASS |  | PASS
X-105 | Concentrate Outlet | 1 | 9 | 9 | llm_estimate | model estimate (no itemised inputs) | parametric | 5 | low | Concentrate Outlet | N/A — proprietary assembly / bought-out package, see datasheet | bottom-up parametric | commodity — MPN at procurement | PASS |  | PASS
X-130 | Sample Valves | 1 | 18 | 18 | llm_estimate | model estimate (no itemised inputs) | catalogue | 5 | low | Sample Valves | PVC-U / 304 stainless (WRAS) | catalogue · MoC: PVC-U / 304 stainless (WRAS) for potable-water service (WRAS-approved wetted materials) | Swagelok SS-42GS4 | PASS |  | PASS
X-131 | Flexmount Connectors | 1 | 1 | 1 | llm_estimate | model estimate (no itemised inputs) | parametric | 5 | low | Flexmount Connectors | N/A — proprietary assembly / bought-out package, see datasheet | bottom-up parametric | commodity — MPN at procurement | PASS |  | PASS
X-132 | Painted Carbon Steel Skid Frame · 2.3 m dia x 2.4 m | 1 | 40 | 40 | class_reference | class-reference price (no itemised inputs) |  | 4 | low | Painted Carbon Steel Skid Frame · 2.3 m dia x 2.4 m | painted structural carbon steel (S275/S355) | made-to-spec · structural budget estimate | bespoke fabrication to drawing — see sizing basis | PASS |  | PASS
F-3 | Grp Membrane Housings · 364 m² area | 1 | 11000 | 11000 | llm_estimate | 364 m²; 37 m² | × 8; take-off; parametric | 5 | low | Grp Membrane Housings · 364 m² area | membrane/filtration media | membrane-housing parametric: 364 m² membrane area ÷ 37 m²/element → 10 × 8-in GRP pressure housing @ £1,100 (UK-2026 supply; NOT a steel take-off) | bespoke fabrication to drawing — see sizing basis | PASS |  | PASS
—.1 | ↳ Pressure Vessel Shell · 15 m³/h | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
—.2 | ↳ Filter Media / Membrane Elements | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
—.3 | ↳ Upper Distribution Header | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
—.4 | ↳ Lower Underdrain / Nozzle Plate | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
—.5 | ↳ Backwash / Service Valve Nest | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
—.6 | ↳ Differential-Pressure Gauges | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
—.7 | ↳ Air Scour / Vent | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
—.8 | ↳ Sample Cock | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
—.9 | ↳ Skid Frame & Pipework | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
—.10 | ↳ Nameplate | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
X-133 | Painted Steel Skid Frame · 2.3 m dia x 2.4 m | 1 | 40 | 40 | class_reference | class-reference price (no itemised inputs) |  | 4 | low | Painted Steel Skid Frame · 2.3 m dia x 2.4 m | painted structural carbon steel (S275/S355) | made-to-spec · structural budget estimate | bespoke fabrication to drawing — see sizing basis | PASS |  | PASS
X-134 | Sst304 Skid Frame · 2.3 m dia x 2.4 m | 1 | 40 | 40 | class_reference | class-reference price (no itemised inputs) |  | 4 | low | Sst304 Skid Frame · 2.3 m dia x 2.4 m | 304 stainless steel | made-to-spec · structural budget estimate | bespoke fabrication to drawing — see sizing basis | PASS |  | PASS
X-135 | Leveling Feet | 1 | 3 | 3 | llm_estimate | model estimate (no itemised inputs) | parametric | 5 | low | Leveling Feet | N/A — proprietary assembly / bought-out package, see datasheet | bottom-up parametric · commodity-floor (estimate £0.11 renders £0; 'feet' → £3) | commodity — MPN at procurement | PASS |  | PASS
TX-101 | Transformer · 75 kW · 1090x927x1199 mm | 1 | 3000 | 3000 | llm_estimate | 75 kVA | £28/kVA; install; rating-based | 5 | low | Transformer · 75 kW · 1090x927x1199 mm | N/A — proprietary assembly / bought-out package, see datasheet | rating-based: 75 kVA × £28/kVA (UK-2026 installed mid; band £15-55/kVA) — transformer @ £/kVA [£15 below band → grounded to market] | TBD (detailed design) | PASS |  | PASS
V-109 | Pressure Relief Valve · 4 kW · 600x510x660 mm | 1 | 18 | 18 | llm_estimate | model estimate (no itemised inputs) | catalogue | 5 | low | Pressure Relief Valve · 4 kW · 600x510x660 mm | PVC-U / 304 stainless (WRAS) | catalogue · MoC: PVC-U / 304 stainless (WRAS) for potable-water service (WRAS-approved wetted materials) | Goetze Series 851 | PASS |  | PASS
I-111 | Low Pressure Switch | 1 | 76 | 76 | class_reference | class-reference price (no itemised inputs) | catalogue | 4 | moderate | Low Pressure Switch | N/A — proprietary assembly / bought-out package, see datasheet | catalogue | Danfoss 060-121966 | PASS |  | PASS
I-112 | High Pressure Switch | 1 | 76 | 76 | class_reference | class-reference price (no itemised inputs) | catalogue | 4 | moderate | High Pressure Switch | N/A — proprietary assembly / bought-out package, see datasheet | catalogue | Danfoss 060-310266 | PASS |  | PASS
X-136 / X-139 | Emergency Stop | 2 | 40 | 80 | class_reference | class-reference price (no itemised inputs) | floored; catalogue | 4 | moderate | Emergency Stop Button | N/A — proprietary assembly / bought-out package, see datasheet | catalogue · floored to min credible price | Eaton 216516 | PASS |  | PASS
I-102 | Electrical Control Cabinet | 1 | 8023 | 8023 | class_reference | 0 m²; 0 bar | £90/m²; take-off | 4 | low | Electrical Control Cabinet | structural steel | structural steelwork take-off: 0 m² plan × £90/m² (UK-2026 fabricated + erected; service=structural, dry, 0 bar — NOT a pressure shell) + £8k connections | Rittal VX25 8284.500 | PASS |  | PASS
X-137 | Cable Trays | 1 | 45 | 45 | class_reference | class-reference price (no itemised inputs) | catalogue | 4 | low | Cable Trays | N/A — proprietary assembly / bought-out package, see datasheet | catalogue | Legrand SRFL100G | PASS |  | PASS
X-138 | Overcurrent Protection | 1 | 6 | 6 | class_reference | class-reference price (no itemised inputs) | catalogue | 4 | low | Overcurrent Protection | N/A — proprietary assembly / bought-out package, see datasheet | catalogue | Schneider Electric LV430630 | PASS |  | PASS
I-113 | Leak Detection Sensor | 1 | 12 | 12 | class_reference | class-reference price (no itemised inputs) | catalogue | 4 | low | Leak Detection Sensor | N/A — proprietary assembly / bought-out package, see datasheet | catalogue | nVent Raychem TT-1000 | PASS |  | PASS
X-140 | Motor Overload Protection | 1 | 96 | 96 | catalogue | catalogue-class budget (no itemised inputs) | catalogue | 4 | moderate | Motor Overload Protection | N/A — proprietary assembly / bought-out package, see datasheet | catalogue | Siemens 3RU2126-4DB0 | PASS |  | PASS
I-114 | Emergency Stop Switch | 1 | 159 | 159 | catalogue | catalogue-class budget (no itemised inputs) | catalogue | 2 | high | Emergency Stop Switch | N/A — proprietary assembly / bought-out package, see datasheet | catalogue | Banner Engineering SSA-EB1PS1-02-A01 | PASS |  | PASS
X-141 | Cable Glands | 1 | 2 | 2 | class_reference | class-reference price (no itemised inputs) | catalogue | 4 | moderate | Cable Glands | N/A — proprietary assembly / bought-out package, see datasheet | catalogue | Cabletec CG-M20-IP68 | PASS |  | PASS
TK-102 / TK-101 | Cip Tank · 1.4 m dia x 1.3 m | 2 | 4000 | 8000 | class_reference | 6 mm; 1.3 m; 13 kPa; 18 MPa; 7 m²; 89 kg; median £8,082, n | ×1.3; × 89; £12.0/kg; × 1.25; 42%; £3,404→£4,000; lifted; | 4 | low | Cleaning Tank · 1.4 m dia x 1.3 m | FRP/GRP | tapered wall 6 mm = P·r/(σ·E)+c · ⌀1.4×1.3 m (open top (no head)) · P=13 kPa head · σ=18 MPa → 7 m² × 89 kg FRP/GRP @ £12.0/kg supply × 1.25 erection + fittings · lifted £3,404→£4,000 to the engine corpus p25 (median £8,082, n=5; line was 42% of median — under-priced vs the engine's own forge-truth reference) | bespoke fabrication to drawing — see sizing basis | PASS |  | PASS
TK-102.1 / TK-101.1 | ↳ Tank Wall (laminate) | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
TK-102.2 / TK-101.2 | ↳ Tank Floor (graded to centre) | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
TK-102.3 / TK-101.3 | ↳ Dual Drain / Centre Standpipe | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
TK-102.4 / TK-101.4 | ↳ Side Drain & Overflow | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
TK-102.5 / TK-101.5 | ↳ Inlet Distribution Ring | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
TK-102.6 / TK-101.6 | ↳ Internal Flow Baffles | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
TK-102.7 / TK-101.7 | ↳ Rim Stiffener | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
TK-102.8 / TK-101.8 | ↳ Access Walkway & Handrail | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
TK-102.9 / TK-101.9 | ↳ Internal Gelcoat / Lining | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
TK-102.10 / TK-101.10 | ↳ Earthing Boss | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
TK-102.11 / TK-101.11 | ↳ Nameplate | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
X-142 | 3 Part Union Fittings | 1 | 9 | 9 | llm_estimate | model estimate (no itemised inputs) | parametric | 5 | low | 3 Part Union Fittings | N/A — proprietary assembly / bought-out package, see datasheet | bottom-up parametric | commodity — MPN at procurement | PASS |  | PASS
C01 | water connection: Gac Softener → Softener Vessel · 14.5 m3/h | 1 | 905 | 905 | pipe £66/m @ DN80 (HDPE/ | 10.8 m; 25 m³; 1.4 m | £66/m; × 10.8; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Gac Softener → Softener Vessel · 14.5 m3/h | HDPE/PVC-U | pipe £66/m @ DN80 (HDPE/PVC-U) × 10.8 m + 2 ends · sized 25 m³/h @ 1.4 m/s · branch duty (default — endpoint not on main loop) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN80 HDPE/PVC-U pipe, 10.8 m | PASS |  | PASS
C02 | water connection: Gac Softener → Drain Collection Sump · 45 m3/h | 1 | 911 | 911 | pipe £36/m @ DN32 (HDPE/ | 20.4 m; 5 m³; 1.7 m | £36/m; × 20.4; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Gac Softener → Drain Collection Sump · 45 m3/h | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 20.4 m + 2 ends · sized 5 m³/h @ 1.7 m/s · bleed/drain duty (~make-up balance) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN32 HDPE/PVC-U pipe, 20.4 m | PASS |  | PASS
C03 | water connection: Uf Module Bank → Ro High Pressure Pump · 11 m3/h | 1 | 1614 | 1614 | pipe £66/m @ DN80 (HDPE/ | 21.5 m; 25 m³; 1.4 m | £66/m; × 21.5; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Uf Module Bank → Ro High Pressure Pump · 11 m3/h | HDPE/PVC-U | pipe £66/m @ DN80 (HDPE/PVC-U) × 21.5 m + 2 ends · sized 25 m³/h @ 1.4 m/s · branch duty (default — endpoint not on main loop) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN80 HDPE/PVC-U pipe, 21.5 m | PASS |  | PASS
C04 | water connection: Uf Module Bank → Drain Collection Sump · 45 m3/h | 1 | 975 | 975 | pipe £36/m @ DN32 (HDPE/ | 22.1 m; 5 m³; 1.7 m | £36/m; × 22.1; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Uf Module Bank → Drain Collection Sump · 45 m3/h | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 22.1 m + 2 ends · sized 5 m³/h @ 1.7 m/s · bleed/drain duty (~make-up balance) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN32 HDPE/PVC-U pipe, 22.1 m | PASS |  | PASS
C05 | water connection: Ro High Pressure Pump → Reverse Osmosis Skid · 11 m3/h | 1 | 2232 | 2232 | pipe £66/m @ DN80 (HDPE/ | 30.9 m; 25 m³; 1.4 m | £66/m; × 30.9; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Ro High Pressure Pump → Reverse Osmosis Skid · 11 m3/h | HDPE/PVC-U | pipe £66/m @ DN80 (HDPE/PVC-U) × 30.9 m + 2 ends · sized 25 m³/h @ 1.4 m/s · branch duty (default — endpoint not on main loop) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN80 HDPE/PVC-U pipe, 30.9 m | PASS |  | PASS
C06 | water connection: Ro High Pressure Pump → Drain Collection Sump · 45 m3/h | 1 | 1443 | 1443 | pipe £36/m @ DN32 (HDPE/ | 35.1 m; 5 m³; 1.7 m | £36/m; × 35.1; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Ro High Pressure Pump → Drain Collection Sump · 45 m3/h | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 35.1 m + 2 ends · sized 5 m³/h @ 1.7 m/s · bleed/drain duty (~make-up balance) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN32 HDPE/PVC-U pipe, 35.1 m | PASS |  | PASS
C07 | water connection: Cloth Filter → Gac Filter · 80 m3/h | 1 | 1403 | 1403 | pipe £66/m @ DN80 (HDPE/ | 18.3 m; 25 m³; 1.4 m | £66/m; × 18.3; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Cloth Filter → Gac Filter · 80 m3/h | HDPE/PVC-U | pipe £66/m @ DN80 (HDPE/PVC-U) × 18.3 m + 2 ends · sized 25 m³/h @ 1.4 m/s · branch duty (default — endpoint not on main loop) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN80 HDPE/PVC-U pipe, 18.3 m | PASS |  | PASS
C08 | water connection: Cloth Filter → Drain Collection Sump · 45 m3/h | 1 | 1014 | 1014 | pipe £36/m @ DN32 (HDPE/ | 23.2 m; 5 m³; 1.7 m | £36/m; × 23.2; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Cloth Filter → Drain Collection Sump · 45 m3/h | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 23.2 m + 2 ends · sized 5 m³/h @ 1.7 m/s · bleed/drain duty (~make-up balance) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN32 HDPE/PVC-U pipe, 23.2 m | PASS |  | PASS
C09 | water connection: Gac Filter → Uv Disinfection · 90 m3/h | 1 | 1559 | 1559 | pipe £66/m @ DN80 (HDPE/ | 20.7 m; 25 m³; 1.4 m; 45 m³ | £66/m; × 20.7; × 2; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Gac Filter → Uv Disinfection · 90 m3/h | HDPE/PVC-U | pipe £66/m @ DN80 (HDPE/PVC-U) × 20.7 m + 2 ends · sized 25 m³/h @ 1.4 m/s · branch duty (default — endpoint not on main loop) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) · demand-sized: peak irrigation demand = 45 m³/h per department × 2 departments | DN80 HDPE/PVC-U pipe, 20.7 m | PASS |  | PASS
C10 | water connection: Gac Filter → Drain Collection Sump · 45 m3/h | 1 | 1243 | 1243 | pipe £36/m @ DN32 (HDPE/ | 29.6 m; 5 m³; 1.7 m | £36/m; × 29.6; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Gac Filter → Drain Collection Sump · 45 m3/h | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 29.6 m + 2 ends · sized 5 m³/h @ 1.7 m/s · bleed/drain duty (~make-up balance) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN32 HDPE/PVC-U pipe, 29.6 m | PASS |  | PASS
C11 | water connection: Uv Disinfection → Drain Collection Sump · 45 m3/h | 1 | 1176 | 1176 | pipe £36/m @ DN32 (HDPE/ | 27.7 m; 5 m³; 1.7 m | £36/m; × 27.7; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Uv Disinfection → Drain Collection Sump · 45 m3/h | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 27.7 m + 2 ends · sized 5 m³/h @ 1.7 m/s · bleed/drain duty (~make-up balance) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN32 HDPE/PVC-U pipe, 27.7 m | PASS |  | PASS
C12 | water connection: Drain Collection Sump → Drain Water Tank · 45 m3/h | 1 | 601 | 601 | pipe £36/m @ DN32 (HDPE/ | 11.7 m; 5 m³; 1.7 m | £36/m; × 11.7; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Drain Collection Sump → Drain Water Tank · 45 m3/h | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 11.7 m + 2 ends · sized 5 m³/h @ 1.7 m/s · bleed/drain duty (~make-up balance) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN32 HDPE/PVC-U pipe, 11.7 m | PASS |  | PASS
C13 | water connection: Drain Collection Sump → Uv Disinfection · 90 m3/h | 1 | 984 | 984 | pipe £36/m @ DN32 (HDPE/ | 22.4 m; 5 m³; 1.7 m; 45 m³ | £36/m; × 22.4; × 2; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Drain Collection Sump → Uv Disinfection · 90 m3/h | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 22.4 m + 2 ends · sized 5 m³/h @ 1.7 m/s · bleed/drain duty (~make-up balance) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) · demand-sized: peak irrigation demand = 45 m³/h per department × 2 departments | DN32 HDPE/PVC-U pipe, 22.4 m | PASS |  | PASS
C14 | water connection: Drain Collection Sump → Hand Watering Pump · 25 m3/h | 1 | 1228 | 1228 | pipe £36/m @ DN32 (HDPE/ | 29.2 m; 5 m³; 1.7 m | £36/m; × 29.2; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Drain Collection Sump → Hand Watering Pump · 25 m3/h | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 29.2 m + 2 ends · sized 5 m³/h @ 1.7 m/s · bleed/drain duty (~make-up balance) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN32 HDPE/PVC-U pipe, 29.2 m | PASS |  | PASS
C15 | water connection: Drain Collection Sump → Cloth Filter · 80 m3/h | 1 | 826 | 826 | pipe £36/m @ DN32 (HDPE/ | 18.0 m; 5 m³; 1.7 m | £36/m; × 18.0; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Drain Collection Sump → Cloth Filter · 80 m3/h | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 18.0 m + 2 ends · sized 5 m³/h @ 1.7 m/s · bleed/drain duty (~make-up balance) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN32 HDPE/PVC-U pipe, 18.0 m | PASS |  | PASS
C16 | water connection: Drain Collection Sump → Gac Softener · 14.5 m3/h | 1 | 508 | 508 | pipe £36/m @ DN32 (HDPE/ | 9.2 m; 5 m³; 1.7 m | £36/m; × 9.2; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Drain Collection Sump → Gac Softener · 14.5 m3/h | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 9.2 m + 2 ends · sized 5 m³/h @ 1.7 m/s · bleed/drain duty (~make-up balance) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN32 HDPE/PVC-U pipe, 9.2 m | PASS |  | PASS
C17 | water connection: Drain Collection Sump → Irrigation Pump · 90 m3/h | 1 | 1131 | 1131 | pipe £36/m @ DN32 (HDPE/ | 26.5 m; 5 m³; 1.7 m; 45 m³ | £36/m; × 26.5; × 2; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Drain Collection Sump → Irrigation Pump · 90 m3/h | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 26.5 m + 2 ends · sized 5 m³/h @ 1.7 m/s · bleed/drain duty (~make-up balance) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) · demand-sized: peak irrigation demand = 45 m³/h per department × 2 departments | DN32 HDPE/PVC-U pipe, 26.5 m | PASS |  | PASS
C18 | water connection: Drain Collection Sump → Reverse Osmosis Skid · 45 m3/h | 1 | 352 | 352 | pipe £36/m @ DN32 (HDPE/ | 4.8 m; 5 m³; 1.7 m | £36/m; × 4.8; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Drain Collection Sump → Reverse Osmosis Skid · 45 m3/h | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 4.8 m + 2 ends · sized 5 m³/h @ 1.7 m/s · bleed/drain duty (~make-up balance) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN32 HDPE/PVC-U pipe, 4.8 m | PASS |  | PASS
C19 | water connection: Drain Collection Sump → Ro High Pressure Pump · 11 m3/h | 1 | 1265 | 1265 | pipe £36/m @ DN32 (HDPE/ | 30.2 m; 5 m³; 1.7 m | £36/m; × 30.2; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Drain Collection Sump → Ro High Pressure Pump · 11 m3/h | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 30.2 m + 2 ends · sized 5 m³/h @ 1.7 m/s · bleed/drain duty (~make-up balance) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN32 HDPE/PVC-U pipe, 30.2 m | PASS |  | PASS
C20 | water connection: Drain Collection Sump → Gac Filter · 45 m3/h | 1 | 1033 | 1033 | pipe £36/m @ DN32 (HDPE/ | 23.8 m; 5 m³; 1.7 m | £36/m; × 23.8; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Drain Collection Sump → Gac Filter · 45 m3/h | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 23.8 m + 2 ends · sized 5 m³/h @ 1.7 m/s · bleed/drain duty (~make-up balance) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN32 HDPE/PVC-U pipe, 23.8 m | PASS |  | PASS
C21 | water connection: Drain Collection Sump → Uf Module Bank · 45 m3/h | 1 | 479 | 479 | pipe £36/m @ DN32 (HDPE/ | 8.4 m; 5 m³; 1.7 m | £36/m; × 8.4; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Drain Collection Sump → Uf Module Bank · 45 m3/h | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 8.4 m + 2 ends · sized 5 m³/h @ 1.7 m/s · bleed/drain duty (~make-up balance) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN32 HDPE/PVC-U pipe, 8.4 m | PASS |  | PASS
C22 | water connection: Drain Collection Sump → Cleaning Tank · 4 m3/h | 1 | 901 | 901 | pipe £36/m @ DN32 (HDPE/ | 20.1 m; 5 m³; 1.7 m | £36/m; × 20.1; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Drain Collection Sump → Cleaning Tank · 4 m3/h | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 20.1 m + 2 ends · sized 5 m³/h @ 1.7 m/s · bleed/drain duty (~make-up balance) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN32 HDPE/PVC-U pipe, 20.1 m | PASS |  | PASS
C23 | water connection: Drain Collection Sump → Cip Tank · 4 m3/h | 1 | 1032 | 1032 | pipe £36/m @ DN32 (HDPE/ | 23.7 m; 5 m³; 1.7 m | £36/m; × 23.7; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Drain Collection Sump → Cip Tank · 4 m3/h | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 23.7 m + 2 ends · sized 5 m³/h @ 1.7 m/s · bleed/drain duty (~make-up balance) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN32 HDPE/PVC-U pipe, 23.7 m | PASS |  | PASS
C24 | water connection: Drain Water Tank → Drain Transfer Pump · 45 m3/h | 1 | 1209 | 1209 | pipe £36/m @ DN32 (HDPE/ | 28.6 m; 5 m³; 1.7 m | £36/m; × 28.6; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Drain Water Tank → Drain Transfer Pump · 45 m3/h | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 28.6 m + 2 ends · sized 5 m³/h @ 1.7 m/s · bleed/drain duty (~make-up balance) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN32 HDPE/PVC-U pipe, 28.6 m | PASS |  | PASS
C25 | water connection: Drain Transfer Pump → Cip Tank · 4 m3/h | 1 | 1161 | 1161 | pipe £36/m @ DN32 (HDPE/ | 27.3 m; 5 m³; 1.7 m | £36/m; × 27.3; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Drain Transfer Pump → Cip Tank · 4 m3/h | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 27.3 m + 2 ends · sized 5 m³/h @ 1.7 m/s · bleed/drain duty (~make-up balance) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN32 HDPE/PVC-U pipe, 27.3 m | PASS |  | PASS
C26 | water connection: Cip Tank → Cleaning Tank · 4 m3/h | 1 | 398 | 398 | pipe £66/m @ DN80 (HDPE/ | 3.1 m; 25 m³; 1.4 m | £66/m; × 3.1; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Cip Tank → Cleaning Tank · 4 m3/h | HDPE/PVC-U | pipe £66/m @ DN80 (HDPE/PVC-U) × 3.1 m + 2 ends · sized 25 m³/h @ 1.4 m/s · branch duty (default — endpoint not on main loop) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN80 HDPE/PVC-U pipe, 3.1 m | PASS |  | PASS
C27 | water connection: Cip Tank → Drain Collection Sump · 45 m3/h | 1 | 913 | 913 | pipe £36/m @ DN32 (HDPE/ | 20.4 m; 5 m³; 1.7 m | £36/m; × 20.4; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Cip Tank → Drain Collection Sump · 45 m3/h | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 20.4 m + 2 ends · sized 5 m³/h @ 1.7 m/s · bleed/drain duty (~make-up balance) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN32 HDPE/PVC-U pipe, 20.4 m | PASS |  | PASS
C28 | water connection: Cleaning Tank → Fresh Water Tank · 4 m3/h | 1 | 670 | 670 | pipe £36/m @ DN32 (HDPE/ | 13.7 m; 5 m³; 1.7 m | £36/m; × 13.7; 0.4%; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Cleaning Tank → Fresh Water Tank · 4 m3/h | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 13.7 m + 2 ends · sized 5 m³/h @ 1.7 m/s · make-up water duty (~0.4% of recirc) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN32 HDPE/PVC-U pipe, 13.7 m | PASS |  | PASS
C29 | water connection: Cleaning Tank → Drain Collection Sump · 45 m3/h | 1 | 1051 | 1051 | pipe £36/m @ DN32 (HDPE/ | 24.3 m; 5 m³; 1.7 m | £36/m; × 24.3; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Cleaning Tank → Drain Collection Sump · 45 m3/h | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 24.3 m + 2 ends · sized 5 m³/h @ 1.7 m/s · bleed/drain duty (~make-up balance) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN32 HDPE/PVC-U pipe, 24.3 m | PASS |  | PASS
C30 | water connection: Fresh Water Tank → Nutrient Tank · — | 1 | 358 | 358 | pipe £36/m @ DN32 (HDPE/ | 5.0 m; 5 m³; 1.7 m | £36/m; × 5.0; 0.4%; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Fresh Water Tank → Nutrient Tank · — | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 5.0 m + 2 ends · sized 5 m³/h @ 1.7 m/s · make-up water duty (~0.4% of recirc) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN32 HDPE/PVC-U pipe, 5.0 m | PASS |  | PASS
C31 | water connection: Fresh Water Tank → Permeate Outlet · 90 m3/h | 1 | 1280 | 1280 | pipe £36/m @ DN32 (HDPE/ | 30.6 m; 5 m³; 1.7 m; 45 m³ | £36/m; × 30.6; 0.4%; × 2; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Fresh Water Tank → Permeate Outlet · 90 m3/h | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 30.6 m + 2 ends · sized 5 m³/h @ 1.7 m/s · make-up water duty (~0.4% of recirc) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) · demand-sized: peak irrigation demand = 45 m³/h per department × 2 departments | DN32 HDPE/PVC-U pipe, 30.6 m | PASS |  | PASS
C32 | water connection: Fresh Water Tank → Softener Vessel · 14.5 m3/h | 1 | 1299 | 1299 | pipe £36/m @ DN32 (HDPE/ | 31.1 m; 5 m³; 1.7 m | £36/m; × 31.1; 0.4%; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Fresh Water Tank → Softener Vessel · 14.5 m3/h | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 31.1 m + 2 ends · sized 5 m³/h @ 1.7 m/s · make-up water duty (~0.4% of recirc) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN32 HDPE/PVC-U pipe, 31.1 m | PASS |  | PASS
C33 | water connection: Fresh Water Tank → Drain Collection Sump · 45 m3/h | 1 | 1158 | 1158 | pipe £36/m @ DN32 (HDPE/ | 27.2 m; 5 m³; 1.7 m | £36/m; × 27.2; 0.4%; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Fresh Water Tank → Drain Collection Sump · 45 m3/h | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 27.2 m + 2 ends · sized 5 m³/h @ 1.7 m/s · make-up water duty (~0.4% of recirc) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN32 HDPE/PVC-U pipe, 27.2 m | PASS |  | PASS
C34 | water connection: Fresh Water Tank → Drain Transfer Pump · 45 m3/h | 1 | 1493 | 1493 | pipe £36/m @ DN32 (HDPE/ | 36.5 m; 5 m³; 1.7 m | £36/m; × 36.5; 0.4%; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Fresh Water Tank → Drain Transfer Pump · 45 m3/h | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 36.5 m + 2 ends · sized 5 m³/h @ 1.7 m/s · make-up water duty (~0.4% of recirc) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN32 HDPE/PVC-U pipe, 36.5 m | PASS |  | PASS
C35 | water connection: Fresh Water Tank → Drain Water Tank · — | 1 | 897 | 897 | pipe £36/m @ DN32 (HDPE/ | 20.0 m; 5 m³; 1.7 m | £36/m; × 20.0; 0.4%; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Fresh Water Tank → Drain Water Tank · — | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 20.0 m + 2 ends · sized 5 m³/h @ 1.7 m/s · make-up water duty (~0.4% of recirc) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN32 HDPE/PVC-U pipe, 20.0 m | PASS |  | PASS
C36 | water connection: Fertigation Dosing Pump → Hand Watering Pump · 25 m3/h | 1 | 1004 | 1004 | pipe £28/m @ DN20 (HDPE/ | 29.6 m; 2 m³; 1.8 m | £28/m; × 29.6; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Fertigation Dosing Pump → Hand Watering Pump · 25 m3/h | HDPE/PVC-U | pipe £28/m @ DN20 (HDPE/PVC-U) × 29.6 m + 2 ends · sized 2 m³/h @ 1.8 m/s · chemical-dosing branch duty · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN20 HDPE/PVC-U pipe, 29.6 m | PASS |  | PASS
C37 | water connection: Fertigation Dosing Pump → Drain Collection Sump · 45 m3/h | 1 | 875 | 875 | pipe £36/m @ DN32 (HDPE/ | 19.4 m; 5 m³; 1.7 m | £36/m; × 19.4; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Fertigation Dosing Pump → Drain Collection Sump · 45 m3/h | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 19.4 m + 2 ends · sized 5 m³/h @ 1.7 m/s · bleed/drain duty (~make-up balance) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN32 HDPE/PVC-U pipe, 19.4 m | PASS |  | PASS
C38 | water connection: Hand Watering Pump → Irrigation Pump · 90 m3/h | 1 | 625 | 625 | pipe £66/m @ DN80 (HDPE/ | 6.5 m; 25 m³; 1.4 m; 45 m³ | £66/m; × 6.5; × 2; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Hand Watering Pump → Irrigation Pump · 90 m3/h | HDPE/PVC-U | pipe £66/m @ DN80 (HDPE/PVC-U) × 6.5 m + 2 ends · sized 25 m³/h @ 1.4 m/s · branch duty (default — endpoint not on main loop) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) · demand-sized: peak irrigation demand = 45 m³/h per department × 2 departments | DN80 HDPE/PVC-U pipe, 6.5 m | PASS |  | PASS
C39 | water connection: Hand Watering Pump → Drain Collection Sump · 45 m3/h | 1 | 1384 | 1384 | pipe £36/m @ DN32 (HDPE/ | 33.5 m; 5 m³; 1.7 m | £36/m; × 33.5; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Hand Watering Pump → Drain Collection Sump · 45 m3/h | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 33.5 m + 2 ends · sized 5 m³/h @ 1.7 m/s · bleed/drain duty (~make-up balance) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN32 HDPE/PVC-U pipe, 33.5 m | PASS |  | PASS
C40 | water connection: Irrigation Pump → Distribution Manifold · 45 m3/h | 1 | 406 | 406 | pipe £104/m @ DN125 (HDP | 1.9 m; 60 m³; 1.4 m | £104/m; × 1.9; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Irrigation Pump → Distribution Manifold · 45 m3/h | HDPE/PVC-U | pipe £104/m @ DN125 (HDPE/PVC-U) × 1.9 m + 2 ends · sized 60 m³/h @ 1.4 m/s · distribution/header branch duty · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN125 HDPE/PVC-U pipe, 1.9 m | PASS |  | PASS
C41 | water connection: Irrigation Pump → Drain Collection Sump · 45 m3/h | 1 | 1296 | 1296 | pipe £36/m @ DN32 (HDPE/ | 31.1 m; 5 m³; 1.7 m | £36/m; × 31.1; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Irrigation Pump → Drain Collection Sump · 45 m3/h | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 31.1 m + 2 ends · sized 5 m³/h @ 1.7 m/s · bleed/drain duty (~make-up balance) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN32 HDPE/PVC-U pipe, 31.1 m | PASS |  | PASS
C42 | electrical connection: Mains Incomer → Standby Diesel Generator · 4.2 A | 1 | 41 | 41 | cable £3/m | 1.5 mm | £3/m·conductor; × 1; ×1; £6/end; × 2; install | 3 | moderate — deterministic take-off (routed length × rate) | electrical connection: Mains Incomer → Standby Diesel Generator · 4.2 A | Cu conductor, LSZH/XLPE insulated (BS 6724/BS 5467 class) | cable £3/m·conductor @ 1.5 mm² × 1 conductor(s) (1∥×1 core) + £6/end-lug × 2 ends · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | 1 × 1.5 mm² Cu, 9.6 m | PASS |  | PASS
C43 | electrical connection: Standby Diesel Generator → Distribution Transformer · 4.2 A | 1 | 36 | 36 | cable £3/m | 1.5 mm | £3/m·conductor; × 1; ×1; £6/end; × 2; install | 3 | moderate — deterministic take-off (routed length × rate) | electrical connection: Standby Diesel Generator → Distribution Transformer · 4.2 A | Cu conductor, LSZH/XLPE insulated (BS 6724/BS 5467 class) | cable £3/m·conductor @ 1.5 mm² × 1 conductor(s) (1∥×1 core) + £6/end-lug × 2 ends · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | 1 × 1.5 mm² Cu, 8.0 m | PASS |  | PASS
C44 | electrical connection: Distribution Transformer → Main Switchboard · 4.2 A | 1 | 74 | 74 | cable £3/m | 1.5 mm | £3/m·conductor; × 1; ×1; £6/end; × 2; install | 3 | moderate — deterministic take-off (routed length × rate) | electrical connection: Distribution Transformer → Main Switchboard · 4.2 A | Cu conductor, LSZH/XLPE insulated (BS 6724/BS 5467 class) | cable £3/m·conductor @ 1.5 mm² × 1 conductor(s) (1∥×1 core) + £6/end-lug × 2 ends · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | 1 × 1.5 mm² Cu, 20.7 m | PASS |  | PASS
C45 | electrical connection: Main Switchboard → Motor Control Center · 4.2 A | 1 | 28 | 28 | cable £3/m | 1.5 mm | £3/m·conductor; × 1; ×1; £6/end; × 2; install | 3 | moderate — deterministic take-off (routed length × rate) | electrical connection: Main Switchboard → Motor Control Center · 4.2 A | Cu conductor, LSZH/XLPE insulated (BS 6724/BS 5467 class) | cable £3/m·conductor @ 1.5 mm² × 1 conductor(s) (1∥×1 core) + £6/end-lug × 2 ends · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | 1 × 1.5 mm² Cu, 5.4 m | PASS |  | PASS
C46 | electrical connection: Motor Control Center → 3 Phase Power Input · 4.2 A | 1 | 29 | 29 | cable £3/m | 1.5 mm | £3/m·conductor; × 1; ×1; £6/end; × 2; install | 3 | moderate — deterministic take-off (routed length × rate) | electrical connection: Motor Control Center → 3 Phase Power Input · 4.2 A | Cu conductor, LSZH/XLPE insulated (BS 6724/BS 5467 class) | cable £3/m·conductor @ 1.5 mm² × 1 conductor(s) (1∥×1 core) + £6/end-lug × 2 ends · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | 1 × 1.5 mm² Cu, 5.7 m | PASS |  | PASS
C47 | electrical connection: Motor Control Center → Uv Disinfection · 8.2 A | 1 | 102 | 102 | cable £3/m | 1.5 mm | £3/m·conductor; × 1; ×1; £6/end; × 2; install | 3 | moderate — deterministic take-off (routed length × rate) | electrical connection: Motor Control Center → Uv Disinfection · 8.2 A | Cu conductor, LSZH/XLPE insulated (BS 6724/BS 5467 class) | cable £3/m·conductor @ 1.5 mm² × 1 conductor(s) (1∥×1 core) + £6/end-lug × 2 ends · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | 1 × 1.5 mm² Cu, 30.1 m | PASS |  | PASS
C48 | electrical connection: Motor Control Center → Fertigation Dosing Pump · 15 A | 1 | 38 | 38 | cable £3/m | 1.5 mm | £3/m·conductor; × 1; ×1; £6/end; × 2; install | 3 | moderate — deterministic take-off (routed length × rate) | electrical connection: Motor Control Center → Fertigation Dosing Pump · 15 A | Cu conductor, LSZH/XLPE insulated (BS 6724/BS 5467 class) | cable £3/m·conductor @ 1.5 mm² × 1 conductor(s) (1∥×1 core) + £6/end-lug × 2 ends · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | 1 × 1.5 mm² Cu, 8.7 m | PASS |  | PASS
C49 | electrical connection: Motor Control Center → Hand Watering Pump · 4.2 A | 1 | 121 | 121 | cable £3/m | 1.5 mm | £3/m·conductor; × 1; ×1; £6/end; × 2; install | 3 | moderate — deterministic take-off (routed length × rate) | electrical connection: Motor Control Center → Hand Watering Pump · 4.2 A | Cu conductor, LSZH/XLPE insulated (BS 6724/BS 5467 class) | cable £3/m·conductor @ 1.5 mm² × 1 conductor(s) (1∥×1 core) + £6/end-lug × 2 ends · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | 1 × 1.5 mm² Cu, 36.4 m | PASS |  | PASS
C50 | electrical connection: Motor Control Center → Drain Transfer Pump · 3.9 A | 1 | 74 | 74 | cable £3/m | 1.5 mm | £3/m·conductor; × 1; ×1; £6/end; × 2; install | 3 | moderate — deterministic take-off (routed length × rate) | electrical connection: Motor Control Center → Drain Transfer Pump · 3.9 A | Cu conductor, LSZH/XLPE insulated (BS 6724/BS 5467 class) | cable £3/m·conductor @ 1.5 mm² × 1 conductor(s) (1∥×1 core) + £6/end-lug × 2 ends · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | 1 × 1.5 mm² Cu, 20.7 m | PASS |  | PASS
C51 | electrical connection: Motor Control Center → Cloth Filter · 4.2 A | 1 | 91 | 91 | cable £3/m | 1.5 mm | £3/m·conductor; × 1; ×1; £6/end; × 2; install | 3 | moderate — deterministic take-off (routed length × rate) | electrical connection: Motor Control Center → Cloth Filter · 4.2 A | Cu conductor, LSZH/XLPE insulated (BS 6724/BS 5467 class) | cable £3/m·conductor @ 1.5 mm² × 1 conductor(s) (1∥×1 core) + £6/end-lug × 2 ends · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | 1 × 1.5 mm² Cu, 26.2 m | PASS |  | PASS
C52 | electrical connection: Motor Control Center → Irrigation Pump · 4.2 A | 1 | 112 | 112 | cable £3/m | 1.5 mm | £3/m·conductor; × 1; ×1; £6/end; × 2; install | 3 | moderate — deterministic take-off (routed length × rate) | electrical connection: Motor Control Center → Irrigation Pump · 4.2 A | Cu conductor, LSZH/XLPE insulated (BS 6724/BS 5467 class) | cable £3/m·conductor @ 1.5 mm² × 1 conductor(s) (1∥×1 core) + £6/end-lug × 2 ends · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | 1 × 1.5 mm² Cu, 33.2 m | PASS |  | PASS
C53 | electrical connection: Motor Control Center → Ro High Pressure Pump · 8.4 A | 1 | 125 | 125 | cable £3/m | 1.5 mm | £3/m·conductor; × 1; ×1; £6/end; × 2; install | 3 | moderate — deterministic take-off (routed length × rate) | electrical connection: Motor Control Center → Ro High Pressure Pump · 8.4 A | Cu conductor, LSZH/XLPE insulated (BS 6724/BS 5467 class) | cable £3/m·conductor @ 1.5 mm² × 1 conductor(s) (1∥×1 core) + £6/end-lug × 2 ends · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | 1 × 1.5 mm² Cu, 37.6 m | PASS |  | PASS
C54 | electrical connection: Motor Control Center → Gac Filter · 4.2 A | 1 | 129 | 129 | cable £3/m | 1.5 mm | £3/m·conductor; × 1; ×1; £6/end; × 2; install | 3 | moderate — deterministic take-off (routed length × rate) | electrical connection: Motor Control Center → Gac Filter · 4.2 A | Cu conductor, LSZH/XLPE insulated (BS 6724/BS 5467 class) | cable £3/m·conductor @ 1.5 mm² × 1 conductor(s) (1∥×1 core) + £6/end-lug × 2 ends · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | 1 × 1.5 mm² Cu, 38.9 m | PASS |  | PASS
C55 | electrical connection: Motor Control Center → Permeate Outlet · 4.2 A | 1 | 86 | 86 | cable £3/m | 1.5 mm | £3/m·conductor; × 1; ×1; £6/end; × 2; install | 3 | moderate — deterministic take-off (routed length × rate) | electrical connection: Motor Control Center → Permeate Outlet · 4.2 A | Cu conductor, LSZH/XLPE insulated (BS 6724/BS 5467 class) | cable £3/m·conductor @ 1.5 mm² × 1 conductor(s) (1∥×1 core) + £6/end-lug × 2 ends · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | 1 × 1.5 mm² Cu, 24.5 m | PASS |  | PASS
C56 | electrical connection: Motor Control Center → Concentrate Outlet · 4.2 A | 1 | 77 | 77 | cable £3/m | 1.5 mm | £3/m·conductor; × 1; ×1; £6/end; × 2; install | 3 | moderate — deterministic take-off (routed length × rate) | electrical connection: Motor Control Center → Concentrate Outlet · 4.2 A | Cu conductor, LSZH/XLPE insulated (BS 6724/BS 5467 class) | cable £3/m·conductor @ 1.5 mm² × 1 conductor(s) (1∥×1 core) + £6/end-lug × 2 ends · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | 1 × 1.5 mm² Cu, 21.5 m | PASS |  | PASS
C57 | water connection: Ultrafiltration Module → Fresh Water Tank · 1.35 m3/h | 1 | 920 | 920 | pipe £36/m @ DN32 (HDPE/ | 20.6 m; 5 m³; 1.7 m | £36/m; × 20.6; 0.4%; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Ultrafiltration Module → Fresh Water Tank · 1.35 m3/h | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 20.6 m + 2 ends · sized 5 m³/h @ 1.7 m/s · make-up water duty (~0.4% of recirc) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN32 HDPE/PVC-U pipe, 20.6 m | PASS |  | PASS
C58 | water connection: Permeate Outlet → Cip Tank · 4 m3/h | 1 | 3550 | 3550 | pipe £66/m @ DN80 (HDPE/ | 50.9 m; 25 m³; 1.4 m | £66/m; × 50.9; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Permeate Outlet → Cip Tank · 4 m3/h | HDPE/PVC-U | pipe £66/m @ DN80 (HDPE/PVC-U) × 50.9 m + 2 ends · sized 25 m³/h @ 1.4 m/s · branch duty (default — endpoint not on main loop) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN80 HDPE/PVC-U pipe, 50.9 m | PASS |  | PASS
C59 | water connection: Softener Vessel → Ultrafiltration Module · 14.5 m3/h | 1 | 1872 | 1872 | pipe £66/m @ DN80 (HDPE/ | 25.4 m; 25 m³; 1.4 m | £66/m; × 25.4; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Softener Vessel → Ultrafiltration Module · 14.5 m3/h | HDPE/PVC-U | pipe £66/m @ DN80 (HDPE/PVC-U) × 25.4 m + 2 ends · sized 25 m³/h @ 1.4 m/s · branch duty (default — endpoint not on main loop) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN80 HDPE/PVC-U pipe, 25.4 m | PASS |  | PASS
C60 | water connection: Nutrient Tank → Drain Collection Sump · 45 m3/h | 1 | 1308 | 1308 | pipe £36/m @ DN32 (HDPE/ | 31.4 m; 5 m³; 1.7 m | £36/m; × 31.4; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Nutrient Tank → Drain Collection Sump · 45 m3/h | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 31.4 m + 2 ends · sized 5 m³/h @ 1.7 m/s · bleed/drain duty (~make-up balance) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN32 HDPE/PVC-U pipe, 31.4 m | PASS |  | PASS
C61 | water connection: Distribution Manifold → Drain Collection Sump · 45 m3/h | 1 | 1344 | 1344 | pipe £36/m @ DN32 (HDPE/ | 32.4 m; 5 m³; 1.7 m | £36/m; × 32.4; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Distribution Manifold → Drain Collection Sump · 45 m3/h | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 32.4 m + 2 ends · sized 5 m³/h @ 1.7 m/s · bleed/drain duty (~make-up balance) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN32 HDPE/PVC-U pipe, 32.4 m | PASS |  | PASS
C62 | water connection: Reverse Osmosis Skid → Drain Collection Sump · 45 m3/h | 1 | 596 | 596 | pipe £36/m @ DN32 (HDPE/ | 11.6 m; 5 m³; 1.7 m | £36/m; × 11.6; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Reverse Osmosis Skid → Drain Collection Sump · 45 m3/h | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 11.6 m + 2 ends · sized 5 m³/h @ 1.7 m/s · bleed/drain duty (~make-up balance) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN32 HDPE/PVC-U pipe, 11.6 m | PASS |  | PASS
C63 | electrical connection: Motor Control Center → Electrical Control Panel · 4.2 A | 1 | 35 | 35 | cable £3/m | 1.5 mm | £3/m·conductor; × 1; ×1; £6/end; × 2; install | 3 | moderate — deterministic take-off (routed length × rate) | electrical connection: Motor Control Center → Electrical Control Panel · 4.2 A | Cu conductor, LSZH/XLPE insulated (BS 6724/BS 5467 class) | cable £3/m·conductor @ 1.5 mm² × 1 conductor(s) (1∥×1 core) + £6/end-lug × 2 ends · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | 1 × 1.5 mm² Cu, 7.5 m | PASS |  | PASS
C64 | electrical connection: Electrical Control Panel → Digital Control Panel · 0.5 A | 1 | 21 | 21 | cable £3/m | 1.5 mm | £3/m·conductor; × 1; ×1; £6/end; × 2; install | 3 | moderate — deterministic take-off (routed length × rate) | electrical connection: Electrical Control Panel → Digital Control Panel · 0.5 A | Cu conductor, LSZH/XLPE insulated (BS 6724/BS 5467 class) | cable £3/m·conductor @ 1.5 mm² × 1 conductor(s) (1∥×1 core) + £6/end-lug × 2 ends · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | 1 × 1.5 mm² Cu, 2.9 m | PASS |  | PASS
C65 | electrical connection: Motor Control Center → Control + Instrument UPS · 4.2 A | 1 | 35 | 35 | cable £3/m | 1.5 mm | £3/m·conductor; × 1; ×1; £6/end; × 2; install | 3 | moderate — deterministic take-off (routed length × rate) | electrical connection: Motor Control Center → Control + Instrument UPS · 4.2 A | Cu conductor, LSZH/XLPE insulated (BS 6724/BS 5467 class) | cable £3/m·conductor @ 1.5 mm² × 1 conductor(s) (1∥×1 core) + £6/end-lug × 2 ends · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | 1 × 1.5 mm² Cu, 7.5 m | PASS |  | PASS
C66 | electrical connection: Control + Instrument UPS → Digital Control Panel · 0.5 A | 1 | 19 | 19 | cable £3/m | 1.5 mm | £3/m·conductor; × 1; ×1; £6/end; × 2; install | 3 | moderate — deterministic take-off (routed length × rate) | electrical connection: Control + Instrument UPS → Digital Control Panel · 0.5 A | Cu conductor, LSZH/XLPE insulated (BS 6724/BS 5467 class) | cable £3/m·conductor @ 1.5 mm² × 1 conductor(s) (1∥×1 core) + £6/end-lug × 2 ends · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | 1 × 1.5 mm² Cu, 2.5 m | PASS |  | PASS
C67 | electrical connection: Motor Control Center → SCADA / Plant Control System · 4.2 A | 1 | 34 | 34 | cable £3/m | 1.5 mm | £3/m·conductor; × 1; ×1; £6/end; × 2; install | 3 | moderate — deterministic take-off (routed length × rate) | electrical connection: Motor Control Center → SCADA / Plant Control System · 4.2 A | Cu conductor, LSZH/XLPE insulated (BS 6724/BS 5467 class) | cable £3/m·conductor @ 1.5 mm² × 1 conductor(s) (1∥×1 core) + £6/end-lug × 2 ends · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | 1 × 1.5 mm² Cu, 7.5 m | PASS |  | PASS
C68 | electrical connection: Motor Control Center → Digital Control Panel · 0.5 A | 1 | 34 | 34 | cable £3/m | 1.5 mm | £3/m·conductor; × 1; ×1; £6/end; × 2; install | 3 | moderate — deterministic take-off (routed length × rate) | electrical connection: Motor Control Center → Digital Control Panel · 0.5 A | Cu conductor, LSZH/XLPE insulated (BS 6724/BS 5467 class) | cable £3/m·conductor @ 1.5 mm² × 1 conductor(s) (1∥×1 core) + £6/end-lug × 2 ends · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | 1 × 1.5 mm² Cu, 7.5 m | PASS |  | PASS
C69 | electrical connection: Motor Control Center → Electrical Control Cabinet · 4.2 A | 1 | 112 | 112 | cable £3/m | 1.5 mm | £3/m·conductor; × 1; ×1; £6/end; × 2; install | 3 | moderate — deterministic take-off (routed length × rate) | electrical connection: Motor Control Center → Electrical Control Cabinet · 4.2 A | Cu conductor, LSZH/XLPE insulated (BS 6724/BS 5467 class) | cable £3/m·conductor @ 1.5 mm² × 1 conductor(s) (1∥×1 core) + £6/end-lug × 2 ends · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | 1 × 1.5 mm² Cu, 33.2 m | PASS |  | PASS
C70 | electrical connection: Electrical Control Cabinet → Digital Control Panel · 0.5 A | 1 | 100 | 100 | cable £3/m | 1.5 mm | £3/m·conductor; × 1; ×1; £6/end; × 2; install | 3 | moderate — deterministic take-off (routed length × rate) | electrical connection: Electrical Control Cabinet → Digital Control Panel · 0.5 A | Cu conductor, LSZH/XLPE insulated (BS 6724/BS 5467 class) | cable £3/m·conductor @ 1.5 mm² × 1 conductor(s) (1∥×1 core) + £6/end-lug × 2 ends · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | 1 × 1.5 mm² Cu, 29.2 m | PASS |  | PASS
C71 | electrical connection: Motor Control Center → Digital Control Panel · — | 1 | 36 | 36 | cable £3/m | 1.5 mm | £3/m·conductor; × 1; ×1; £6/end; × 2; install | 3 | moderate — deterministic take-off (routed length × rate) | electrical connection: Motor Control Center → Digital Control Panel · — | Cu conductor, LSZH/XLPE insulated (BS 6724/BS 5467 class) | cable £3/m·conductor @ 1.5 mm² × 1 conductor(s) (1∥×1 core) + £6/end-lug × 2 ends · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | power feeder, 8.0 m (design current unknown) | PASS |  | PASS
X-143 | Zoned distribution — department delivery mains · DN125 PVC-U · 214 m | 214 | 20.8 | 4451 | parametric | 214 m; 7.7 m; 30 m; 45 m³; 1.3 m; 90 m³ | £20.8/m; 20%; £104/m; × 7.7; × 30; × 5; install; parametri |  |  | Zoned distribution — department delivery mains · DN125 PVC-U · 214 m | PVC-U (thermoplastic pressure pipework, solvent-weld) | parametric estimate — zoned-delivery distribution network (engineered allowance, NOT per-pipe routed; client distribution-section scope): 214 m × £20.8/m supply-only materials (20% of the uk-2026 supply+install £104/m @ DN125; installation labour is carried by the cost-stack field-install factors — no double count) · length-priced: qty = the run length in metres, unit = £/m · derivation: parametric — not routed (zoned-delivery distribution network, engineered allowance): delivery mains (department spines) = 2 group(s) × (10 branches × 7.7 m branch pitch + 30 m plant-room stand-off) = 214 m; DN125 at 45 m³/h ≤ 1.3 m/s (surge-limited delivery main on a cycling valve network) · 200 zones (actuated_distribution_valve_count) × 30 positions/zone (6000 served positions); 2 delivery group(s); 20 branch runs × 5 level(s); fill duty 45 m³/h/group from irrigation_pump_flow_m3_h = 90 m³/h delivered ÷ 2 groups (the irrigation_demand_m3_per_hr = 45 m³/h per-group brief metric) | DN125 PVC-U pressure pipe + fittings + hangers, 214 m (supply) | PASS |  | ⚠ FAIL — 'Est class' empty; 'Confidence' empty
X-144 | Zoned distribution — department delivery mains · DN125 PVC-U · 280 m | 280 | 20.8 | 5824 | parametric | 280 m; 7 m; 1.3 m; 0.5 m; 45 m³; 90 m³ | £20.8/m; 20%; £104/m; × 7; × 1.3; × 30; × 5; install; para |  |  | Zoned distribution — delivery risers · DN125 PVC-U · 280 m | PVC-U (thermoplastic pressure pipework, solvent-weld) | parametric estimate — zoned-delivery distribution network (engineered allowance, NOT per-pipe routed; client distribution-section scope): 280 m × £20.8/m supply-only materials (20% of the uk-2026 supply+install £104/m @ DN125; installation labour is carried by the cost-stack field-install factors — no double count) · length-priced: qty = the run length in metres, unit = £/m · derivation: parametric — not routed (zoned-delivery distribution network, engineered allowance): delivery risers = 40 risers (200 zones ÷ 5 levels) × 7 m (5 levels × 1.3 m tier pitch + 0.5 m) = 280 m; DN125 at 45 m³/h ≤ 1.3 m/s · 200 zones (actuated_distribution_valve_count) × 30 positions/zone (6000 served positions); 2 delivery group(s); 20 branch runs × 5 level(s); fill duty 45 m³/h/group from irrigation_pump_flow_m3_h = 90 m³/h delivered ÷ 2 groups (the irrigation_demand_m3_per_hr = 45 m³/h per-group brief metric) | DN125 PVC-U pressure pipe + fittings + hangers, 280 m (supply) | PASS |  | ⚠ FAIL — 'Est class' empty; 'Confidence' empty
X-145 | Zoned distribution — department delivery mains · DN75 PVC-U · 8,280 m | 8280 | 13.2 | 109296 | parametric | 8,280 m; 2.76 m; 41.4 m; 8280 m; 45 m³; 3.0 m; 90 m³ | £13.2/m; 20%; £66/m; × 2.76; × 41.4; × 30; × 5; install; p |  |  | Zoned distribution — zone laterals (flood-fill lines) · DN75 PVC-U · 8,280 m | PVC-U (thermoplastic pressure pipework, solvent-weld) | parametric estimate — zoned-delivery distribution network (engineered allowance, NOT per-pipe routed; client distribution-section scope): 8,280 m × £13.2/m supply-only materials (20% of the uk-2026 supply+install £66/m @ DN75; installation labour is carried by the cost-stack field-install factors — no double count) · length-priced: qty = the run length in metres, unit = £/m · derivation: parametric — not routed (zoned-delivery distribution network, engineered allowance): zone laterals = 200 zones × (30 positions/zone ÷ 2 rows × 2.76 m position pitch) = 200 × 41.4 m = 8280 m; DN75 at the 45 m³/h open-zone flood-fill duty ≤ 3.0 m/s (short-duration fill) · 200 zones (actuated_distribution_valve_count) × 30 positions/zone (6000 served positions); 2 delivery group(s); 20 branch runs × 5 level(s); fill duty 45 m³/h/group from irrigation_pump_flow_m3_h = 90 m³/h delivered ÷ 2 groups (the irrigation_demand_m3_per_hr = 45 m³/h per-group brief metric) | DN75 PVC-U pressure pipe + fittings + hangers, 8,280 m (supply) | PASS |  | ⚠ FAIL — 'Est class' empty; 'Confidence' empty
X-146 | Zoned distribution — department delivery mains · DN110 PVC-U · 4,200 m | 4200 | 20.8 | 87360 | parametric | 4,200 m; 7 m; 4200 m; 45 m³; 1.4 m; 90 m³ | £20.8/m; 20%; £104/m; × 7; × 30; × 5; install; parametric |  |  | Zoned distribution — drain/return risers (gravity) · DN110 PVC-U · 4,200 m | PVC-U (thermoplastic pressure pipework, solvent-weld) | parametric estimate — zoned-delivery distribution network (engineered allowance, NOT per-pipe routed; client distribution-section scope): 4,200 m × £20.8/m supply-only materials (20% of the uk-2026 supply+install £104/m @ DN110; installation labour is carried by the cost-stack field-install factors — no double count) · length-priced: qty = the run length in metres, unit = £/m · derivation: parametric — not routed (zoned-delivery distribution network, engineered allowance): drain/return risers (mirror of the delivery grid) = 600 gravity drops (an outlet per 2 positions per level) × 7 m = 4200 m; DN110 gravity at 45 m³/h ≤ 1.4 m/s · 200 zones (actuated_distribution_valve_count) × 30 positions/zone (6000 served positions); 2 delivery group(s); 20 branch runs × 5 level(s); fill duty 45 m³/h/group from irrigation_pump_flow_m3_h = 90 m³/h delivered ÷ 2 groups (the irrigation_demand_m3_per_hr = 45 m³/h per-group brief metric) | DN110 PVC-U pressure pipe + fittings + hangers, 4,200 m (supply) | PASS |  | ⚠ FAIL — 'Est class' empty; 'Confidence' empty
X-147 | Zoned distribution — department delivery mains · DN110 PVC-U · 1,656 m | 1656 | 20.8 | 34445 | parametric | 1,656 m; 41.4 m; 1656 m; 1.4 m; 45 m³; 90 m³ | £20.8/m; 20%; £104/m; × 41.4; × 20; × 30; × 5; install; pa |  |  | Zoned distribution — drain collection lines · DN110 PVC-U · 1,656 m | PVC-U (thermoplastic pressure pipework, solvent-weld) | parametric estimate — zoned-delivery distribution network (engineered allowance, NOT per-pipe routed; client distribution-section scope): 1,656 m × £20.8/m supply-only materials (20% of the uk-2026 supply+install £104/m @ DN110; installation labour is carried by the cost-stack field-install factors — no double count) · length-priced: qty = the run length in metres, unit = £/m · derivation: parametric — not routed (zoned-delivery distribution network, engineered allowance): drain collection lines = 2 floor lines/branch × 41.4 m × 20 branches = 1656 m; DN110 gravity ≤ 1.4 m/s · 200 zones (actuated_distribution_valve_count) × 30 positions/zone (6000 served positions); 2 delivery group(s); 20 branch runs × 5 level(s); fill duty 45 m³/h/group from irrigation_pump_flow_m3_h = 90 m³/h delivered ÷ 2 groups (the irrigation_demand_m3_per_hr = 45 m³/h per-group brief metric) | DN110 PVC-U pressure pipe + fittings + hangers, 1,656 m (supply) | PASS |  | ⚠ FAIL — 'Est class' empty; 'Confidence' empty
X-148 | Zoned distribution — department delivery mains · DN160 PVC-U · 214 m | 214 | 35.2 | 7533 | parametric | 214 m; 45 m³; 0.8 m; 90 m³ | £35.2/m; 20%; £176/m; × 30; × 5; install; parametric |  |  | Zoned distribution — main drain headers · DN160 PVC-U · 214 m | PVC-U (thermoplastic pressure pipework, solvent-weld) | parametric estimate — zoned-delivery distribution network (engineered allowance, NOT per-pipe routed; client distribution-section scope): 214 m × £35.2/m supply-only materials (20% of the uk-2026 supply+install £176/m @ DN160; installation labour is carried by the cost-stack field-install factors — no double count) · length-priced: qty = the run length in metres, unit = £/m · derivation: parametric — not routed (zoned-delivery distribution network, engineered allowance): main drain headers = the delivery-spine mirror (214 m); DN160 at 45 m³/h ≤ 0.8 m/s part-full gravity equivalent · 200 zones (actuated_distribution_valve_count) × 30 positions/zone (6000 served positions); 2 delivery group(s); 20 branch runs × 5 level(s); fill duty 45 m³/h/group from irrigation_pump_flow_m3_h = 90 m³/h delivered ÷ 2 groups (the irrigation_demand_m3_per_hr = 45 m³/h per-group brief metric) | DN160 PVC-U pressure pipe + fittings + hangers, 214 m (supply) | PASS |  | ⚠ FAIL — 'Est class' empty; 'Confidence' empty
X-149 | Hand watering — ring main to both departments · DN90 PVC-U · 428 m | 428 | 16.4 | 7019 | parametric | 428 m; 107 m; 45 m³; 90 m³ | £16.4/m; 20%; £82/m; × 2; × 30; × 5; install; parametric |  |  | Hand watering — ring main to both departments · DN90 PVC-U · 428 m | PVC-U (thermoplastic pressure pipework, solvent-weld) | parametric estimate — client section E scope (hand-watering ring main — engineered allowance, NOT per-pipe routed): 428 m × £16.4/m supply-only materials (20% of the uk-2026 supply+install £82/m @ DN90; installation labour is carried by the cost-stack field-install factors — no double count) · length-priced: qty = the run length in metres, unit = £/m · derivation: parametric — not routed (zoned-delivery distribution network, engineered allowance): hand-watering ring main = 2 delivery group(s)/department(s) × 2 legs (ring out-and-return along the 107 m delivery spine, serving every branch head) = 428 m · 200 zones (actuated_distribution_valve_count) × 30 positions/zone (6000 served positions); 2 delivery group(s); 20 branch runs × 5 level(s); fill duty 45 m³/h/group from irrigation_pump_flow_m3_h = 90 m³/h delivered ÷ 2 groups (the irrigation_demand_m3_per_hr = 45 m³/h per-group brief metric) | DN90 PVC-U pressure pipe + fittings + hangers, 428 m (supply) | PASS |  | ⚠ FAIL — 'Est class' empty; 'Confidence' empty
X-150 | Zoned distribution — department delivery mains · 6,000 off | 6000 | 6 | 36000 | parametric | parametric estimate (no itemised inputs) | parametric |  |  | Zoned distribution — delivery inlet stubs, one per served position · 6,000 off | PVC-U (thermoplastic pressure pipework, solvent-weld) | parametric estimate — zoned-delivery distribution network: 6,000 served positions × £6 inlet-stub materials allowance (tee + stub + inlet fitting, ex-works) · parametric — not routed (zoned-delivery distribution network, engineered allowance): one delivery inlet stub + fitting per served position = 6000 | Small-bore PVC-U tee + stub + inlet fitting (supply) | PASS |  | ⚠ FAIL — 'Est class' empty; 'Confidence' empty
X-151 | Zoned distribution — department delivery mains · 3,000 off | 3000 | 9 | 27000 | parametric | parametric estimate (no itemised inputs) | parametric |  |  | Zoned distribution — drain outlet connections (one per 2 positions) · 3,000 off | PVC-U (thermoplastic pressure pipework, solvent-weld) | parametric estimate — zoned-delivery distribution network: 3,000 drain outlets × £9 gravity tee/branch materials allowance (ex-works) · parametric — not routed (zoned-delivery distribution network, engineered allowance): one gravity drain outlet per 2 served positions = 3000 | PVC-U gravity tee/branch outlet fitting (supply) | PASS |  | ⚠ FAIL — 'Est class' empty; 'Confidence' empty
V-110 | Zoned distribution — department delivery mains · 200 off | 200 | 40 | 8000 | parametric | parametric estimate (no itemised inputs) | parametric |  |  | Zoned distribution — zone valve connection kits · 200 off | PVC-U (thermoplastic pressure pipework, solvent-weld) | parametric estimate — zoned-delivery distribution network: 200 valve zones × £40 connection-kit materials allowance; the actuated valve assemblies themselves are priced on their own BoM line (assembly family £/DN) — this kit is the pipework tie-in only, no double count · parametric — not routed (zoned-delivery distribution network, engineered allowance): one zone connection kit (valve stub-in, unions, supports) per sectioning valve = 200 | Zone valve stub-in: unions, supports, riser tie-in (supply; valve body + actuator priced on the actuated-valve assembly line) | PASS |  | ⚠ FAIL — 'Est class' empty; 'Confidence' empty
V-111 | Hand watering — ring main to both departments · 44 off | 44 | 45 | 1980 | parametric | parametric estimate (no itemised inputs) | × 20; install; parametric |  |  | Hand watering — tap/hose stations (riser, hand valve + quick connector) · 44 off | PVC-U (thermoplastic pressure pipework, solvent-weld) | parametric estimate — client section E scope (hand-watering ring main — engineered allowance, NOT per-pipe routed): 44 tap/hose stations × £45 per-station materials allowance (brass hand valve ~£14 + quick-release hose coupler ~£9 + ring-main tee, riser stub + clamps ~£22, ex-works; installation labour is carried by the cost-stack field-install factors — no double count) · parametric — not routed (zoned-delivery distribution network, engineered allowance): hand-watering tap risers (each a hand valve + quick connector) = 2 per branch × 20 branches + 2 per delivery group at the plant/irrigation room (4) = 44 | Ring-main riser stub-in: brass hand valve, quick-release hose coupler, tee + clamps (supply) | PASS |  | ⚠ FAIL — 'Est class' empty; 'Confidence' empty
Σ TOTAL |  |  |  | 815837
Coverage by drawing (parts-ledger.json)
Drawing | Expected | Present | % present | [10 empty] | Cell check
blender | 27 | 27 | 100 | [10 empty] | PASS
general-arrangement | 27 | 27 | 100 | [10 empty] | PASS
pid | 39 | 36 | 92.3 | [10 empty] | PASS
single-line-diagram | 13 | 13 | 100 | [10 empty] | PASS
panel-schedule | 23 | 19 | 82.6 | [10 empty] | PASS
block-flow-diagram | 18 | 18 | 100 | [10 empty] | PASS
process-schedules | 21 | 20 | 95.2 | [10 empty] | PASS
parts-ledger grand_total_gbp |  |  |  | 815837 | Compare against the LIVE Σ line £ at row 403. See the ⚠ Checks tab for the reconciliation row.

## Brief
Brief — original vs engine-enhanced |  | ↑ Contents
⬤ TAB QUALITY 10/10 · PASS (target ≥8, live from the Quality & Audit score cell) · client-offer reconciliation (live section mapping) — client-offer reconciliation sections consistent (incl. decision-covered) 6/6; every live section rendered as a recon… · full audit: Quality & Audit tab
The verbatim client brief (left) and the engine's structured, enhanced interpretation (right) that drives the whole design.
Original brief (verbatim) | Engine-enhanced brief (structured)
Water, Fertigation and Ebb/Flow Irrigation Plant — Indoor Multi-Layer Cultivation Facility | Product summary
We are designing and specifying a complete water-handling, purification, fertigation and ebb/flow irrigation plant that supplies a large indoor multi-layer cultivation facility. The deliverable is the WATER SYSTEM ONLY — the purification train, the water storage, the nutrient-dosing (fertigation) units, the flood-and-drain (ebb/flow) distribution network, the drain-water recovery, a hand-watering ring main, and the irrigation/fertigation process-control computer. This is a process and fluid-handling plant: pumps, pipes, tanks, reverse osmosis, filtration, valves and dosing. The grow-lighting, the climate/heating-ventilation/cooling hardware, the cultivation rack framework and the building are NOT part of this plant — they are supplied by others and are explicitly out of scope. This is modelled on a real turnkey supplier offer (Codema Systems Group, offer 3201262, "Farm 2", 2020) totalling €1,395,019. | Automated water purification, storage, and nutrient-dosing (fertigation) system for indoor controlled-environment agriculture.
Target market: indoor and vertical-farming operators, controlled-environment-agriculture growers, glasshouse and horticulture operators across the United Kingdom and Europe who need a turnkey water-treatment, fertigation and irrigation plant for a multi-layer growing facility.
System description (the six delivered subsystems): | Primary product
A. WATER PURIFICATION — treats incoming potable mains water to the feed quality the growing system needs. | Conditioned, nutrient-dosed irrigation water
​- Reverse-osmosis unit: hourly permeate capacity 8.0 cubic metres per hour, raw-tap-water blending capacity 1.2 to 1.6 cubic metres per hour, recovery factor 75 percent, working pressure 10.6 bar at 15 degrees Celsius feed, minimum inlet pressure 2.1 bar, water supply required at least 10.7 cubic metres per hour, electrical supply 3 by 400 volt plus neutral 50 hertz, total installed 5.5 kilowatts, consumption 4.2 kilowatts; stainless-steel supporting frame with inlet section, pre-filter set, frequency-controlled high-pressure pump, integrated permeate flushing line, a first-water flush, the membranes in high-pressure lines, and a central programmable-logic-controller panel for fully automatic operation. Water-supply connection DN63 polyvinyl-chloride, reject/waste connection DN50, permeate connection DN50.
​- Particle filter: one 80-micron cleanable particle filter in the inlet line of the carbon filter, distributor with 2-inch connections, transparent housing. | Construction materials
​- Granular-activated-carbon filter: nominal filtration capacity 14.5 cubic metres per hour, one 42-inch tank, pressure drop about 0.5 bar, DN80 connections. | Polyvinyl chloride (PVC), stainless steel, galvanized steel, glass-fibre-reinforced plastic (FRP)
​- Water softener: capacity 14.0 cubic metres per hour, minimum 1.75 cubic metres per hour per softener tank, two glass-fibre-reinforced-plastic softener tanks with food-quality strong-acid cation resin (350 litres of resin per tank), automatic brine regeneration with one polyethylene brine vessel holding 355 kilograms of salt; 91 cubic metres treated between regenerations, 35 to 88 kilograms of salt and 2.8 cubic metres of water per regeneration, hardness reduction to 0.1 degrees of hardness or better, 15 watts in operation.
​- Raw-tap-water blending line: adjustable valve and flow indicator on the carbon-filter outlet to blend plus or minus 15 percent of the permeate capacity back into the produced water. | Derived requirements
​- Connection lines: a DN63 polyvinyl-chloride city-water line to the reverse-osmosis unit (within 50 metres), a DN50 polyvinyl-chloride waste line to the sewer, and a DN63 polyvinyl-chloride fresh-water line from the reverse-osmosis unit to the fresh-water tank (within 50 metres). | • RO Feed Water Demand: 10.7 m3/h (stated)
B. WATER STORAGE — galvanised Class-A storage tanks with wall-protection blanket, a 0.6-millimetre black anti-algae liner and a duplex polyurethane-coated lowest ring, set on concrete tiles. | • RO Permeate Production: 8 m3/h (stated)
​- One fresh-water tank, 3.64 metres diameter by 3.88 metres high, 40 cubic metres. | • RO Reject Waste Flow: 2.67 m3/h (derived)
​- Two drain-water tanks, 3.64 metres diameter by 3.88 metres high, 40 cubic metres each. | • Maximum Blended Water Production: 9.6 m3/h (derived)
​- Level monitoring: a 4-channel level processor with one pressure sensor per tank. | • Total Irrigation Flow Capacity: 90 m3/h (derived)
​- Suction lines: DN110 polyvinyl-chloride from the fresh-water tank to the hand-watering unit; DN160 polyvinyl-chloride suction lines from the fresh-water tank to each of the two fertiliser units and from each drain-water tank to its fertiliser unit; each with a butterfly valve and a bottom connection. | • Irrigation Delivery Pressure: 3.5 bar (stated)
C. FERTILISER (FERTIGATION) UNITS — two A/B nutrient-dosing units, each 45 cubic metres per hour, for the multi-layer ebb/flow system, dosing the A and B fertiliser streams simultaneously by suction. Each unit consists of: | • Total Water Storage Capacity: 120 m3 (derived)
​- a stainless-steel frame with adjustable supports; | • Drain Water Recovery Storage: 80 m3 (derived)
​- two 125-millimetre Keystone Composeal manual butterfly valves and two 125-millimetre check valves; | • Fertiliser Stock Inventory: 8000 L (derived)
​- one double-action electrically-operated 125-millimetre Keystone Composeal valve for reusing drain water, with an electrical-conductivity supply measuring sensor; | • Softener Regeneration Interval: 8.5 h (derived)
​- one Lowara e-SHE 50-160/75 circulation pump, 7.5 kilowatts, 45 cubic metres per hour at 3.5 bar, with thermostat and polyvinyl-chloride flanges; | • Maximum Salt Consumption Rate: 10.3 kg/h (derived)
​- one 0-to-10-bar pressure sensor for the frequency controller; | • Total Major Pump Installed Power: 20.5 kW (derived)
​- an A-B dosing system on the simultaneous-suction principle: a stainless-steel motorised control unit, two polyvinyl-chloride venturi injectors, two flowmeters, two membrane control valves, and two shunt lines on the pump suction/discharge; | • Softener Resin Volume: 700 L (derived)
​- an electrical-conductivity / pH measuring shunt (110-millimetre, Hoogendoorn): a bypass line with a 25-millimetre tube, two ball valves, and electrical-conductivity and pH sensors; | • Target Water Hardness: 0.1 dH (stated)
​- one acid dosing pump (Iwaki EWN-C21VCER) with a 100-litre barrel, and one chemical dosing pump (Iwaki EWN-C21VHERA) with a 100-litre barrel;
​- one 90-millimetre paddle-wheel flowmeter and one 110-millimetre check valve. | Operating conditions
Each unit has a pump switch panel (main switch, magnet switch, thermal protection, control/alarm relays, manual start, indication lamps, acoustic and free-potential alarm, Danfoss frequency controller). Nutrient stock: eight 1,000-litre polyester fertiliser tanks (four A, four B) with hinged covers and suction sets, and eight electric mixers on stainless-steel frames. | • ro_feed_temperature: 15 C (stated)
D. EBB/FLOW (FLOOD-AND-DRAIN) IRRIGATION INSTALLATION — the flood-and-drain distribution and drain network for the cultivation containers. | • ro_working_pressure: 10.6 bar (stated)
​- Layout: 2 departments, 10 cultivation tunnels per department, 5 layers per tunnel, 4 rows per layer, 15 containers per row — 6,000 cultivation containers total, each 2,760 by 1,290 millimetres; flood depth 15 millimetres; one inlet per container at 1.5 cubic metres per hour; 30 containers per valve, 200 electrically-actuated valves; one valve per department open at a time, giving a maximum demand of 45 cubic metres per hour per department. | • ro_minimum_inlet_pressure: 2.1 bar (stated)
​- Mainlines: DN125 polyvinyl-chloride main line from each fertiliser unit to its department, with two riser connections per tunnel. | • electrical_supply: 400V 3-phase + Neutral, 50Hz (stated)
​- Risers, valves, distribution: two DN125 risers per cultivation room, each riser fitted with five 2.5-inch electric valves; each valve section feeds 30 containers (two rows of 15) via a DN75 distribution line running the length of the tunnel, with an inlet to each container.
​- Drain lines: a DN110 outlet per two containers to a DN110 riser (five outlets per riser, one per layer), 15 risers per tunnel side to a DN110 floor drain line, collected into a DN160 main drain line per compartment running to the drain pit. | Notes
​- Drain-water pit: a 5,000-litre drain pit per cultivation room with a 45-cubic-metre-per-hour submersible pump discharging through a DN110 line to the cloth filter. | The brief incorrectly classified the system as a 'continuous chemical process with solvent recovery'. It is actually a batch/continuous water purification, storage, and fertigation plant for horticulture. Grow-lighting, HVAC, and civil works are explicitly excluded from the scope.
​- Cloth-filter unit: an 80-cubic-metre-per-hour cloth filter per cultivation room on a high-density-polyethylene tank, with a self-priming 45-cubic-metre-per-hour pump returning the filtered drain water to the drain-water tank for reuse.
E. HAND-WATERING INSTALLATION — a frequency-controlled pump, 25 cubic metres per hour at 3.0 bar, on a stainless-steel frame, feeding a DN90 polyvinyl-chloride hand-watering ring main to both departments with 44 risers (two per tunnel plus four at the irrigation room), each with a hand valve and a quick connector.
F. PROCESS-CONTROL COMPUTER — a horticultural irrigation/fertigation process computer (Hoogendoorn iSii class) managing the irrigation scheduling, the closed-loop electrical-conductivity and pH correction, level and flow monitoring, and the safety and fault alarms. Hardware: the process computer in a cabinet, two monitors, a 750-volt-ampere uninterruptible power supply, a radiation sensor, an Ethernet-CAN interface, and 22 distributed datapoint input/output casings. Water hardware: two pulse/litre counters, two inductive electrical-conductivity sensors and transmitters, two pH sensors, two pH transmitters, two pH-sensor armatures. Bus terminals: 4-channel digital-input, 4-to-20-milliamp and 0-to-20-milliamp analogue-input, and 55 four-channel digital-output AC/DC terminals. Software functions: two irrigation units with pump, 200 valves, two electrical-conductivity controls, two pH controls, two pH checks, two 16-choice fertiliser-selection groups, 20 crop sections, 20 registration groups, 20 recipes. Control cabling: control-bus and multi-core signal cable runs (500 to 2,000 metres each).
Key constraints (the brief's target metrics):
​- Total cultivation containers (trays): approximately 6,000 (the irrigation network sizing driver)
​- Maximum irrigation demand: approximately 45 cubic metres per hour per department (two departments)
​- Reverse-osmosis permeate capacity: approximately 8 cubic metres per hour at approximately 75 percent recovery
​- Granular-activated-carbon and softener throughput: approximately 14 to 14.5 cubic metres per hour
​- Water-storage capacity: three tanks of approximately 40 cubic metres each (one fresh, two drain)
​- Fertigation: two A/B dosing units of approximately 45 cubic metres per hour, each with an approximately 7.5-kilowatt circulation pump at approximately 3.5 bar, closed-loop electrical-conductivity and pH correction, and eight 1,000-litre nutrient stock tanks (four A, four B)
​- Hand watering: approximately 25 cubic metres per hour at approximately 3 bar
​- Pipework: thermoplastic (polyvinyl-chloride) pressure pipework throughout, DN50 to DN160, sized for the stated flows
​- Electrical supply: 400 volt, three-phase, 50 hertz; the design must state the connected and average electrical load (the plant is pumps, dosing and controls — of the order of low tens of kilowatts, NOT megawatts)
​- Number of actuated valves: approximately 200
​- Design life: 20 years
​- Annual production volume: 6 units per year
​- Unit cost ceiling: approximately £1,250,000 to £1,400,000 installed for the water, storage, fertigation, irrigation and control plant
​- Primary objective: balanced — the lowest installed cost that meets the irrigation throughput, the water-purity and the layout targets
Cost and calibration context (the real Codema offer — the ground truth the engine must reproduce):
​- A. Water purification: approximately £85,000 (€94,735)
​- B. Water storage: approximately £31,000 (€34,553)
​- C. Fertiliser/fertigation units: approximately £92,000 (€102,234)
​- D. Ebb/flow irrigation installation: approximately £895,000 (€993,750) — the dominant cost, overwhelmingly installed polyvinyl-chloride pipework, the approximately 200 actuated valves, the risers and the drain network, plus installation labour, NOT major equipment
​- E. Hand watering: approximately £24,000 (€26,857)
​- F. Process-control computer: approximately £128,000 (€142,890)
​- Total: approximately £1,250,000 (€1,395,019)
​- The ebb/flow irrigation network (D) is roughly 71 percent of the total, so the bill of materials and the cost build-up must capture the long pipe runs, the approximately 200 actuated valves, the risers and the drain network — not just the major equipment.
Safety and regulatory:
​- Pressure Systems Safety Regulations for the pressurised vessels and the reverse-osmosis high-pressure section
​- Control of Substances Hazardous to Health assessment for the acid and concentrated-nutrient dosing chemicals (corrosive; segregated bunded storage, eyewash and personal protective equipment)
​- Water Supply (Water Fittings) Regulations and backflow prevention on the mains connection (Fluid Category protection)
​- Machinery Directive, Low Voltage Directive and Electromagnetic Compatibility Directive for the equipment
​- Legionella / water-hygiene control on the stored and recirculated water
​- UKCA marking
Explicitly EXCLUDED (out of scope — supplied by others, per the Codema exemptions):
​- the grow-lighting / assimilation lighting and its switchboards
​- the climate / heating, ventilation and cooling hardware and the climate-control computer
​- the cultivation rack framework
​- the building, civil works and excavation
​- the main electrical switchboard and the feeder cables to it, and earthing/cable tray/cable penetrations
Sub-modules expected: mains water intake and backflow protection, water softening, granular-activated-carbon filtration, particle filtration, reverse-osmosis purification and blending, fresh-water and drain-water storage with level monitoring, A/B nutrient dosing and electrical-conductivity/pH correction, nutrient stock-tank storage and mixing, ebb/flow distribution mains/risers/actuated valve sections, gravity drain collection and drain pit, drain-water cloth filtration and return, hand-watering ring main, irrigation/fertigation process-control and instrumentation, and the control cabling.
Client offer vs this design, by subsystem
Mapping: each BoM line is classed to a client section by its SERVICE/SCOPE family — the MOST SPECIFIC subsystem keyword match wins (ties in the client's own A→F order); an interconnect line follows its service (electrical/control cabling → the controls section; pipework touching the distribution/drain network → that section; other process runs → their source endpoint's section); plant-wide field instrumentation → the controls-and-instrumentation section. Each row states WHICH line families it counted. Unallocated lines are shown separately, NEVER forced into a match, and Σ sections + unallocated equals the bill total EXACTLY (asserted at build). The client's section prices are INSTALLED, so the comparison column is the engine installed-equivalent = section BoM materials × 1.7 (this run's installed ÷ materials ratio from the cost stack). Recorded scope decisions (briefs-loop/fischer_farms_codema.decisions.json) render inline: a diverging section covered by a decision reads CONSISTENT WITH RECORDED DECISION (who/date/rationale + the real numbers); a diverging section with NO recorded decision still fails.
Client section | Client offer £ (installed) | This design £ (BoM materials) | Installed-equivalent £ | Δ vs offer £ | Honest note | Cell check
A. Water purification | 85000 | 102880 | 174896 | 89896 | CONSISTENT WITH RECORDED DECISION — engine 2.1× the client section (installed-equiv £174,896 vs client £85,000). The engine's fuller purification design stands versus the leaner client offer — accepted scope, not a defect to tune away. — Tristan Fischer, 2026-07-03. Rationale: The engine includes an ultrafiltration membrane bank, ultraviolet disinfection and duplicated granular-activated-carbon/softener treatment trains that the client's offer never priced; the whole-plant total remains ~1.1x the client's GBP 1,250,000 offer. [evidence: engine installed-equivalent ~2.3x the client section (v61: GBP 198,958 vs GBP 85,000); whole-plant total 1.11x] · COUNTED: 12× section scope stems (most-specific match) £90,228 · 7× process interconnect (by source endpoint) £12,652 | PASS
B. Water storage | 31000 | 45349 | 77093 | 46093 | CONSISTENT WITH RECORDED DECISION — engine 2.5× the client section (installed-equiv £77,093 vs client £31,000). The engine's fuller tank scope stands versus the leaner client offer — accepted scope, not a defect to tune away. — Tristan Fischer, 2026-07-03. Rationale: The engine prices fuller installed tank scope (~GBP 23k per installed 40 m3 galvanised tank vs the client's ~GBP 10k) plus level instrumentation the client's offer never priced; the whole-plant total remains ~1.1x the client's GBP 1,250,000 offer. [evidence: engine installed-equivalent ~2.4x the client section (v61: GBP 74,465 vs GBP 31,000); whole-plant total 1.11x] · COUNTED: 2× section scope stems (most-specific match) £40,845 · 4× process interconnect (by source endpoint) £3,834 · 1× process interconnect (by destination endpoint) £670 | PASS
C. Fertiliser/fertigation units | 92000 | 41024 | 69741 | -22259 | engine installed-equivalent within 24% of the client section · COUNTED: 2× section scope stems (most-specific match) £40,020 · 1× process interconnect (by source endpoint) £1,004 | PASS
D. Ebb/flow irrigation installation | 895000 | 438702 | 745793 | -149207 | engine installed-equivalent within 17% of the client section · COUNTED: 16× section scope stems (most-specific match) £405,378 · 33× distribution/drain-network pipework £33,324 | PASS
E. Hand watering | 24000 | 11499 | 19548 | -4452 | engine installed-equivalent within 19% of the client section · COUNTED: 3× section scope stems (most-specific match) £11,499 | PASS
F. Process-control computer | 128000 | 140533 | 238906 | 110906 | CONSISTENT WITH RECORDED DECISION — engine 1.9× the client section (installed-equiv £238,906 vs client £128,000). The engine's fuller controls-and-instrumentation design stands versus the leaner client offer — accepted scope, not a defect to tune away. — Tristan Fischer, 2026-07-03. Rationale: The engine includes a SCADA/process-control system plus plant-wide field instrumentation (17 banded level transmitters and the electrical/control cabling) that the client's single process-control-computer line never priced; the whole-plant total remains ~1.1x the client's GBP 1,250,000 offer. [evidence: engine installed-equivalent ~1.8x the client section (v61: GBP 234,124 vs GBP 128,000); whole-plant total 1.11x] · COUNTED: 24× section scope stems (most-specific match) £86,868 · 18× field instrumentation (plant-wide) £52,076 · 24× electrical/control cabling £1,589 | PASS
(engine lines not mapped to any client section) |  | 35850 |  |  | engine-added scope with no client section counterpart (e.g. standby power, skid frames, CIP) — kept VISIBLY unallocated, never forced into a section · COUNTED: 25× no section family match £35,452 · 1× interconnect with no in-scope endpoint £398 | PASS
TOTAL | 1250000 | 815837 | 1360613 | 110613 | engine installed capex (cost stack) vs the client's total offer

## Design basis
Design-basis statement — codes, duties, fluid & utilisation basis | [5 empty] | ↑ Contents
⬤ TAB QUALITY 10/10 · PASS (target ≥8, live from the Quality & Audit score cell) · arithmetic: 10 × min(sourced 26/26, unit-or-ratio 26/26, cross-ref resolves 3/3); content checks: design-basis completeness arithmetic — basis rows carrying a value + a … · full audit: Quality & Audit tab
The rules this design was ACTUALLY sized to, one page. Every line is DERIVED LIVE from the module that owns it (pipe/duct sizing constants, the electrical model's BS 7671 ladder, ISO 3098 print legibility, the contract quantities, the Inputs utilisation drivers) with its source stated — never hand-typed. Change the rule at source and this statement follows on rebuild. The Cross-ref check column formula-verifies every live Inputs-tab reference actually resolves to a populated cell.
Discipline | Item | Value | Unit | Source (module constant / contract quantity — never hand-typed) | Cross-ref check | Cell check
Process & piping
Process & piping | Pipe sizing basis — target velocity, liquid lines | 1.5 | m/s | connection_sizing.DEFAULT_LIQUID_VELOCITY_MS — D = √(4Q/πv), next standard DN up | n/a (static value — not a cross-reference) | PASS
Process & piping | Target velocity, gas / vapour lines | 18 | m/s | connection_sizing.DEFAULT_GAS_VELOCITY_MS | n/a (static value — not a cross-reference) | PASS
Process & piping | Target velocity, steam lines | 30 | m/s | connection_sizing.DEFAULT_STEAM_VELOCITY_MS | n/a (static value — not a cross-reference) | PASS
Process & piping | Velocity limit, liquid lines (line-list spec) | 3 | m/s | connection_sizing.LIQUID_VELOCITY_LIMIT_MS — the ≤ limit every line is checked against | n/a (static value — not a cross-reference) | PASS
Process & piping | Velocity limit, gas lines (erosion) | 30 | m/s | connection_sizing.GAS_VELOCITY_LIMIT_MS (API RP 14E erosion ballpark) | n/a (static value — not a cross-reference) | PASS
Process & piping | Velocity limit, steam lines (erosion) | 45 | m/s | connection_sizing.STEAM_VELOCITY_LIMIT_MS | n/a (static value — not a cross-reference) | PASS
Process & piping | Standard pipe size ladder | DN15–DN300 (14 standard bores) | DN | connection_sizing.PIPE_DN_LADDER — the ONE ladder the sizer, line list and BoM share | n/a (static value — not a cross-reference) | PASS
HVAC
HVAC | Duct sizing basis — target air velocity | 6 | m/s | draw_hvac.DEFAULT_DUCT_VELOCITY_MS — duct area = airflow ÷ target velocity | n/a (static value — not a cross-reference) | PASS
HVAC | Duct velocity ceiling (flagged above) | 9 | m/s | draw_hvac.DUCT_VELOCITY_MAX_MS | n/a (static value — not a cross-reference) | PASS
Electrical
Electrical | Distribution voltage (this design) | 400 V 3-ph LV |  | electrical_distribution_model.select_distribution_voltage(53 kW) — 53 kW ≤ 250 kW → standard 400 V LV board | n/a (static value — not a cross-reference) | PASS
Electrical | Cable conductor sizes — preferred ladder | 1.5–400 (17 sizes) | mm² | electrical_distribution_model.CABLE_CSA_LADDER — BS 7671 / IEC 60228 preferred sizes | n/a (static value — not a cross-reference) | PASS
Electrical | Cable ampacity basis | BS 7671 Method C (conservative single-core copper) |  | electrical_distribution_model._CSA_AMPACITY_A | n/a (static value — not a cross-reference) | PASS
Electrical | Assumed displacement power factor | 0.95 |  | electrical_distribution_model.POWER_FACTOR (stated, kW↔A) | n/a (static value — not a cross-reference) | PASS
Electrical | Practical LV main-board current ceiling | 2500 | A | electrical_distribution_model.PRACTICAL_LV_BOARD_CURRENT_A — past this the model steps up | n/a (static value — not a cross-reference) | PASS
Drawings
Drawings | Minimum lettering on printed A1 sheets | 2.5 | mm | a1_print.MIN_TEXT_MM — ISO 3098 minimum lettering height; pagination splits a drawing onto more A1 sheets until met | n/a (static value — not a cross-reference) | PASS
Design flows & duties
Design flows & duties | fertigation dosing capacity m3 per hr | 90 | m³/h | orchestratorContract.quantities.fertigation_dosing_capacity_m3_per_hr (calculator) | n/a (static value — not a cross-reference) | PASS
Design flows & duties | fertigation dosing total m3 h | 90 | m3/h | orchestratorContract.quantities.fertigation_dosing_total_m3_h (demand-coverage) | n/a (static value — not a cross-reference) | PASS
Design flows & duties | irrigation demand m3 h | 90 | m³/h | orchestratorContract.quantities.irrigation_demand_m3_h (calculator) | n/a (static value — not a cross-reference) | PASS
Design flows & duties | irrigation pump flow m3 h | 90 | m3/h | orchestratorContract.quantities.irrigation_pump_flow_m3_h (tool:irrigation:pump-sizing) | n/a (static value — not a cross-reference) | PASS
Design flows & duties | uv disinfection throughput m3 h | 90 | m³/h | orchestratorContract.quantities.uv_disinfection_throughput_m3_h (calculator) | n/a (static value — not a cross-reference) | PASS
Design flows & duties | transformer kva | 75 | kVA | orchestratorContract.quantities.transformer_kva (tool:electrical:transformer-sizing) | n/a (static value — not a cross-reference) | PASS
Design flows & duties | connected electrical load kw | 53 | kW | orchestratorContract.quantities.connected_electrical_load_kw (calculator) | n/a (static value — not a cross-reference) | PASS
Process fluid
Process fluid | Design fluid density | 1000 | kg/m³ | process-fluid density (median of 3 engine worked-calc input(s)) — resolved by _process_fluid_density from the engine's own worked-calc inputs | n/a (static value — not a cross-reference) | PASS
Utilisation drivers
Utilisation drivers | Water / service utilisation (levelised-cost divisor) | 0.25 |  | LIVE ← 'Inputs & Assumptions'!$B$14 — annual delivered volume = design flow × 8760 × THIS driver | ✓ live — resolves to 0.25 | PASS
Utilisation drivers | Electrical load factor (energy line only) | 0.65 |  | LIVE ← 'Inputs & Assumptions'!$B$11 — average÷peak electrical ratio — sizes the energy cost, never the water divisor | ✓ live — resolves to 0.65 | PASS
Utilisation drivers | Operating hours basis | 8000 | h/yr | LIVE ← 'Inputs & Assumptions'!$B$12 — hours per year the plant runs | ✓ live — resolves to 8000 | PASS

## Drawings
Drawing register | [13 empty] | ↑ Contents
⬤ TAB QUALITY 9.6/10 · PASS (target ≥8, live from the Quality & Audit score cell) · drawing-register integrity: every registered A1 print PDF exists on disk + ISO 3098 2.5 mm lettering bar — registered drawings with their print set present 4/4; cell com… · full audit: Quality & Audit tab
Every engineering drawing and render in this dossier. The File column names the print-ready ISO A1 vector PDF set in the run's drawings/ folder (841 × 594 mm, smallest lettering ≥ 2.5 mm on paper per ISO 3098; multi-sheet drawings carry match lines). The workbook tabs embed reduced PNG previews — print from the A1 PDFs, never from the previews. Gates is the drawing's own G1-G9 deterministic verdict (drawing_gates.py); the footer row formula-checks that every registered drawing shares ONE revision and ONE issue date.
Drawing No. | Title | Rev | Date | Scale | Sheets | Min lettering | File (A1 print set) | Preview tab | File check | Gates (G1-G9) | Audit: PDFs found | Audit: missing sheets | Audit: gates failing | Audit: gates pass (1/0) | Cell check
FF-GA-001 | General Arrangement | P1 | 2026-07-04 | 1:200 (@ A1) | 1 | 2.89 mm | drawings/ga-A1.pdf | GA — General Arrangement | ✓ 1 sheet PDF(s) on disk | ✓ G1-G9 all pass | 1 |  |  | 1 | PASS
FF-PID-001 | Piping & Instrumentation Diagram | P1 | 2026-07-04 | NTS | 12 | 3.25 mm | drawings/pid-A1.pdf drawings/pid-A1-sheet2.pdf drawings/pid-A1-sheet3.pdf drawings/pid-A1-sheet4.pdf drawings/pid-A1-sheet5.pdf drawings/pid-A1-sheet6.pdf drawings/pid-A1-sheet7.pdf drawings/pid-A1-sheet8.pdf drawings/pid-A1-sheet9.pdf drawings/pid-A1-sheet10.pdf drawings/pid-A1-sheet11.pdf drawings/pid-A1-sheet12.pdf | P&ID | ✓ 12 sheet PDF(s) on disk | ✓ G1-G9 all pass | 12 |  |  | 1 | PASS
FF-BFD-001 | Block Flow Diagram | P1 | 2026-07-04 | NTS | 6 | 2.7 mm | drawings/bfd-A1.pdf drawings/bfd-A1-sheet2.pdf drawings/bfd-A1-sheet3.pdf drawings/bfd-A1-sheet4.pdf drawings/bfd-A1-sheet5.pdf drawings/bfd-A1-sheet6.pdf | BFD — Block Flow | ✓ 6 sheet PDF(s) on disk | ✓ G1-G9 all pass | 6 |  |  | 1 | PASS
FF-SLD-001 | Single-Line Electrical Diagram | P1 | 2026-07-04 | NTS | 1 | 3.05 mm | drawings/single-line-A1.pdf | Electrical | ✓ 1 sheet PDF(s) on disk |  | 1 |  |  | 0 | ⚠ FAIL — 'Gates (G1-G9)' empty

## BFD — Block Flow
BFD — Block Flow | ↑ Contents
⬤ TAB QUALITY 10/10 · PASS (target ≥8, live from the Quality & Audit score cell) · block-flow part-coverage arithmetic (parts_ledger) — drawing part coverage (block-flow-diagram) 18/18 · score = min over checks of 10 × passed/checked · full audit: Quality & Audit tab
Block flow diagram of the process. |  | SG: Unsure what this is showing. Process is not usually this straight a line. With flow only going one way at all times?
Full-size vector sheets: drawings/bfd-A1.pdf (sheets 1-6, ISO A1, lettering ≥2.5 mm) — see the Drawings register tab. Reading guide: each block is one major process step — follow the stream arrows left to right; block names match the Quantities and BoM module groupings.

## P&ID
P&ID | ↑ Contents
⬤ TAB QUALITY 9/10 · PASS (target ≥8, live from the Quality & Audit score cell) · P&ID part-coverage arithmetic (parts_ledger ✓/✗ vs the BoM) — drawing part coverage (pid) 36/39 · score = min over checks of 10 × passed/checked · full audit: Quality & Audit tab
Piping & instrumentation diagram.
SG: Seems all sensors on left are plugged into a softener vessel?
Full-size vector sheets: drawings/pid-A1.pdf (sheets 1-12, ISO A1, lettering ≥2.5 mm) — see the Drawings register tab. Reading guide: top band = the process train in flow order (follow the numbered lines left to right), lower band = utility / dosing tie-ins; line numbers match the Process schedules tab. |  | SG: RO water feeds into cloth filter which doesn't make sense as its clean already. Why is filter media separate to the cloth filter? Filters and disinfection should be after drain pits as the water needs to be pumped back above ground. Drain pits suggest a lott of undergrouond civils work but previous pages suggest almost no civils costs and all above ground pipework in the render but this is not the case. Does number of sensors and pumps etc match the P&ID. I don't know what the "CIP tank" or "Cleaning Tank" are doing or why they are there? And then they feed into a fresh water tank so that is not a fresh water tank. Then this feeds into nutrient ank. Then all pumps are in a line but they would not all be connected they'd be separate. I think this could be a long way off correct.

## Process schedules
Process schedules | [8 empty] | ↑ Contents
⬤ TAB QUALITY 9.6/10 · PASS (target ≥8, live from the Quality & Audit score cell) · schedule column contract (per-cell completeness + type over every schedule row, from the drawings/*.md source) + cross-schedule item-count reconciliation vs the BoM — cr… · full audit: Quality & Audit tab
Valve list and instrument index — sortable sections parsed from process-schedules.md and cross-referenced to the P&ID. The LINE LIST lives once, on the 'Line & velocity' tab.
Process line list — see the 'Line & velocity' tab
→ Line & velocity | THE line list: every routed line ONCE (as-routed tags, e.g. 201-PR-DN65) with its size, computed flow/velocity vs the erosion band, length, £ and per-row contract check. The 80-row block previously duplicated here carried the same physical lines in two tag dialects, plus artefact rows (a from==to self-loop; 4-20 mA instrument signal cables misfiled as pipes) — signals are on the instrument index below, never the pipe list.
Process valve list
Tag | Type | Service | Line / location | Size | Set / Cv | Fail | P&ID | Cell check
PCV-201 | Control valve | Flow Control Valve (assembly component) | 242-WT-DN20 | DN20 | modulating | FC | FF-PID-001 S1-S12 | PASS
PSV-201 (×2) | Pressure relief (PSV) | Tank Vent / Pressure Relief (assembly component) | V-106 | DN65 | 0.13 bar (design P) — derived from V-106's stated design pressure (13 kPa, basis) | n/a (self-actuated) | FF-PID-001 S1-S12 | PASS
HV-201 (×2) | Manual isolation | Suction Isolation Valve (assembly component) | 201-PR | DN65 | n/a (isolation — full bore) | n/a (manual) | FF-PID-001 S1-S12 | PASS
HV-202 (×2) | Manual isolation | Discharge Isolation Valve (assembly component) | 202-PR | not derivable — Fertigation Dosing Pump states no flow duty (host pump has no m3/h to size a line from) | n/a (isolation — full bore) | n/a (manual) | FF-PID-001 S1-S12 | PASS
NV-201 (×2) | Non-return (check) | Non-Return Valve (assembly component) | 203-PR | not derivable — Fertigation Dosing Pump states no flow duty (host pump has no m3/h to size a line from) | n/a (check — passive) | n/a (passive) | FF-PID-001 S1-S12 | PASS
HV-203 | Manual isolation | Suction Isolation Valve (assembly component) | 204-PR | DN100 — derived from host pump duty (25 m3/h @ 1.3 m/s suction) | n/a (isolation — full bore) | n/a (manual) | FF-PID-001 S1-S12 | PASS
HV-204 | Manual isolation | Discharge Isolation Valve (assembly component) | 205-PR | DN50 | n/a (isolation — full bore) | n/a (manual) | FF-PID-001 S1-S12 | PASS
NV-202 | Non-return (check) | Non-Return Valve (assembly component) | 206-PR | DN50 | n/a (check — passive) | n/a (passive) | FF-PID-001 S1-S12 | PASS
HV-205 (×2) | Manual isolation | Suction Isolation Valve (assembly component) | 242-WT-DN20 | DN20 | n/a (isolation — full bore) | n/a (manual) | FF-PID-001 S1-S12 | PASS
HV-206 (×2) | Manual isolation | Discharge Isolation Valve (assembly component) | 242-WT-DN20 | DN20 | n/a (isolation — full bore) | n/a (manual) | FF-PID-001 S1-S12 | PASS
NV-203 (×2) | Non-return (check) | Non-Return Valve (assembly component) | 242-WT-DN20 | DN20 | n/a (check — passive) | n/a (passive) | FF-PID-001 S1-S12 | PASS
HV-207 | Manual isolation | Suction Isolation Valve (assembly component) | 207-PR | DN200 — derived from host pump duty (90 m3/h @ 1.3 m/s suction) | n/a (isolation — full bore) | n/a (manual) | FF-PID-001 S1-S12 | PASS
HV-208 | Manual isolation | Discharge Isolation Valve (assembly component) | 208-PR | DN125 — derived from host pump duty (90 m3/h @ 2 m/s discharge) | n/a (isolation — full bore) | n/a (manual) | FF-PID-001 S1-S12 | PASS
NV-204 | Non-return (check) | Non-Return Valve (assembly component) | 209-PR | DN125 — derived from host pump duty (90 m3/h @ 2 m/s discharge) | n/a (check — passive) | n/a (passive) | FF-PID-001 S1-S12 | PASS
HV-209 | Manual isolation | Suction Isolation Valve (assembly component) | 210-PR | not derivable — Ro High Pressure Pump states no flow duty (host pump has no m3/h to size a line from) | n/a (isolation — full bore) | n/a (manual) | FF-PID-001 S1-S12 | PASS
HV-210 | Manual isolation | Discharge Isolation Valve (assembly component) | 211-PR | DN125 | n/a (isolation — full bore) | n/a (manual) | FF-PID-001 S1-S12 | PASS
NV-205 | Non-return (check) | Non-Return Valve (assembly component) | 212-WT | not derivable — Ro High Pressure Pump states no flow duty (host pump has no m3/h to size a line from) | n/a (check — passive) | n/a (passive) | FF-PID-001 S1-S12 | PASS
XV-201 | Solenoid shut-off | Solenoid Valve | 213-WT | — | on/off (tight-shutoff) | FC | FF-PID-001 S1-S12 | ⚠ FAIL — 'Size' placeholder '—'
XV-202 (×200) | Actuated isolation | Pneumatic Actuated Valves | 214-PR | DN32 | on/off (tight-shutoff) | FC | FF-PID-001 S1-S12 | PASS
PCV-202 | Control valve | Flow Control Valves | 242-WT-DN20 | DN20 | modulating | FC | FF-PID-001 S1-S12 | PASS
FCV-201–202 | Control valve | DN100 modulating control valve (45 m³/h @ 2 m/s), on the inlet of Softener Vessel; modulated against the tank level transmitter to balance the recirculation flow | 242-WT-DN20 | DN20 | modulating | FC | FF-PID-001 S1-S12 | PASS
XV-203 | Solenoid shut-off | Solenoid Valve | 215-PR | DN32 | on/off (tight-shutoff) | FC | FF-PID-001 S1-S12 | PASS
PCV-203 | Control valve | Pneumatic Control Valve | 216-WT | DN32 | modulating | FC | FF-PID-001 S1-S12 | PASS
PSV-202 | Pressure relief (PSV) | Pressure Relief Valve | V-106 | DN65 | 0.13 bar (design P) — derived from V-106's stated design pressure (13 kPa, basis) | n/a (self-actuated) | FF-PID-001 S1-S12 | PASS
Process instruments
Tag | ISA | Service | Measured | Type | Location | Range | Signal | Loop | Cell check
PT-218 | PT | Differential-Pressure Gauges — TBD (detailed design) | Pressure | Coplanar gauge / DP | X-912 | — | 4–20 mA | FF-PID-001 S1-S12 | ⚠ FAIL — 'Range' placeholder '—'
PT-219 | PT | Differential-Pressure Gauges — TBD (detailed design) | Pressure | Coplanar gauge / DP | Z-102 | — | 4–20 mA | FF-PID-001 S1-S12 | ⚠ FAIL — 'Range' placeholder '—'
PT-220…224 | PT | Discharge Pressure Gauge — TBD (detailed design) | Pressure | Coplanar gauge / DP | P-101 (4 off) | — | 4–20 mA | FF-PID-001 S1-S12 | ⚠ FAIL — 'Range' placeholder '—'
PT-222 | PT | Discharge Pressure Gauge — TBD (detailed design) | Pressure | Coplanar gauge / DP | P-101 | — | 4–20 mA | FF-PID-001 S1-S12 | ⚠ FAIL — 'Range' placeholder '—'
PT-225 | PT | Differential-Pressure Gauges — TBD (detailed design) | Pressure | Coplanar gauge / DP | V-103 | — | 4–20 mA | FF-PID-001 S1-S12 | ⚠ FAIL — 'Range' placeholder '—'
PT-226 | PT | Discharge Pressure Gauge — TBD (detailed design) | Pressure | Coplanar gauge / DP | P-101 | — | 4–20 mA | FF-PID-001 S1-S12 | ⚠ FAIL — 'Range' placeholder '—'
PT-227 | PT | Differential-Pressure Gauges — TBD (detailed design) | Pressure | Coplanar gauge / DP | P-101 | — | 4–20 mA | FF-PID-001 S1-S12 | ⚠ FAIL — 'Range' placeholder '—'
PT-228 | PT | Discharge Pressure Gauge — TBD (detailed design) | Pressure | Coplanar gauge / DP | P-101 | — | 4–20 mA | FF-PID-001 S1-S12 | ⚠ FAIL — 'Range' placeholder '—'
PT-229 | PT | Differential-Pressure Gauges — TBD (detailed design) | Pressure | Coplanar gauge / DP | P-101 | — | 4–20 mA | FF-PID-001 S1-S12 | ⚠ FAIL — 'Range' placeholder '—'
PT-230 | PT | Differential-Pressure Gauges — TBD (detailed design) | Pressure | Coplanar gauge / DP | X-912 | — | 4–20 mA | FF-PID-001 S1-S12 | ⚠ FAIL — 'Range' placeholder '—'
PT-231 | PT | Differential-Pressure Gauges — TBD (detailed design) | Pressure | Coplanar gauge / DP | X-913 | — | 4–20 mA | FF-PID-001 S1-S12 | ⚠ FAIL — 'Range' placeholder '—'
FT-201 | FT | Flow Meter | Flow | Electromagnetic | lines (e.g. 243-PR-DN32) | — | 4–20 mA | FF-PID-001 S1-S12 | ⚠ FAIL — 'Range' placeholder '—'
AT-202 | AT (pH) | Ph Sensor | pH / conductivity | Memosens electrode | vessels (e.g. V-106) | 0–14 pH | 4–20 mA | FF-PID-001 S1-S12 | PASS
AT-203 | AT (ORP) | Orp Sensor | Redox (ORP) | Pt ORP electrode | vessels (e.g. V-106) | −1500 to +1500 mV | 4–20 mA | FF-PID-001 S1-S12 | PASS
LT-201…213 | LT | Level Transmitter | Level | Guided-radar | vessels (e.g. V-106) (13 off) | 0–1.4 m | 4–20 mA | FF-PID-001 S1-S12 | PASS
LT-214 | LT | Level Transmitter | Level | Guided-radar | Z-101 | 0–3 m | 4–20 mA | FF-PID-001 S1-S12 | PASS
LT-215…217 | LT | Level Transmitter | Level | Guided-radar | vessels (e.g. V-106) (3 off) | 0–4 m | 4–20 mA | FF-PID-001 S1-S12 | PASS
AT-201 | AT (pH) | pH Analyser | pH / conductivity | ISE / glass electrode | TK-114 | 0–14 pH | 4–20 mA | FF-PID-001 S1-S12 | PASS
PT-201…217 | PT | Pressure Transmitter | Pressure | Piezoresistive | P-101 (17 off) | 0–5 bar | 4–20 mA | FF-PID-001 S1-S12 | PASS
AT-204 | AT | Silica Analyzer | Composition | NDIR analyser | vessels (e.g. V-106) | — | 4–20 mA | FF-PID-001 S1-S12 | ⚠ FAIL — 'Range' placeholder '—'
FT-202 | FT | Flow Meter | Flow | Electromagnetic | lines (e.g. 243-PR-DN32) | — | 4–20 mA | FF-PID-001 S1-S12 | ⚠ FAIL — 'Range' placeholder '—'
PT-232 | PT | Differential-Pressure Gauges — TBD (detailed design) | Pressure | Coplanar gauge / DP | X-912 | — | 4–20 mA | FF-PID-001 S1-S12 | ⚠ FAIL — 'Range' placeholder '—'
Cross-schedule consistency — schedule item totals vs the BoM
Check | Measured / compared | Row check | Audit: schedule count | Audit: BoM count |  |  |  |  | Cell check
Valve count: schedule vs BoM | schedule 231 vs BoM 233 (±20% band) | PASS | 231 | 233 |  |  |  |  | PASS
Instrument count: schedule vs BoM | schedule 55 vs BoM 52 (±20% band) | PASS | 55 | 52 |  |  |  |  | PASS

## GA — General Arrangement
GA — General Arrangement | ↑ Contents
⬤ TAB QUALITY 10/10 · PASS (target ≥8, live from the Quality & Audit score cell) · GA mechanism: parts-ledger coverage × default-size litter × layout-divergence × typed-shape checks — drawing part coverage (general-arrangement) 27/27 · score = min over… · full audit: Quality & Audit tab |  | SG: It seems the kit has justt been randomly placed, not bunched together based on e.g. what sides needs maintenance/access and walkways around etc, seems a huge footprint for a 45m3 system,, would be way smaller. This is half of F2 process building for 1 system whereas we had 3 systems in about 1/4 that area. Graphics can't be used for any kind of construction etc not enough details or dimensions, is just a graphic.
General arrangement / plant layout.
Full-size vector sheets: drawings/ga-A1.pdf (sheet 1 of 1, ISO A1, lettering ≥2.5 mm) — see the Drawings register tab. Reading guide: plan view with elevations — equipment outlines carry the same tags as the Part names tab; dimensions in mm, datum ±0.000 = finished floor level.

## HVAC
HVAC | ↑ Contents
⬤ OUT OF SCOPE FOR THIS ARCHETYPE — VERIFIED, NOT SCORED · HVAC duty-scoped check: contract duty signal → drawing coverage; no duty → honest out-of-scope disclosure (capped 8) — confirmed no HVAC/ventilation/cooling contract dut… · full audit: Quality & Audit tab |  | SG: Is this above irrigation? Width dims don't match. Where is the key for this i.e. what is Z-01-06. Seems a weird layout, unsure what it is showing. What is the HVAC required for? What is its design required?
HVAC / ventilation layout.
Full-size vector sheets: drawings/hvac-A1.pdf (sheet 1 of 1, ISO A1, lettering ≥2.5 mm) — see the Drawings register tab. Reading guide: duct runs overlay the GA footprint with supply vs extract airflow arrows; equipment tags match the Part names tab.

## Electrical
Electrical — single-line diagram + panel / load schedule | [10 empty] | ↑ Contents
⬤ TAB QUALITY 9.5/10 · PASS (target ≥8, live from the Quality & Audit score cell) · column-contract arithmetic: 10 × 21/22 rows passing; content checks: panel-schedule column contract + single-line drawing coverage — cell completeness+type contract 179/… · full audit: Quality & Audit tab
The electrical design on ONE tab: single-line diagram (preview) above, the panel / load schedule below. Every number on this tab renders from ONE dataset — the schedule (the converged connection schedule): Design I = P·1000 / (√3·V·pf·η) — pf 0.85 / η 0.90 for motor circuits, pf 1.0 / η 1.0 for resistive loads — from each circuit's INSTALLED motor frame. ΔU % is the cable volt-drop over its length / CSA at Design I. 'In spec' is a LIVE formula = (ΔU ≤ 5 %) — a missing/dash ΔU renders ✗, never a pass. Auto-generated; not for construction. ROW CHECK CONTRACT (score = 10 × rows-passing ÷ rows = 10 × 21/22 = 9.5): Ckt/Description=required_nonempty · Conn. load (kW)=required_nonempty · Design I (A)=computed · Protective device=computed · Cable=computed · Length (m)=required_nonempty · ΔU (%)=computed · In spec=computed · Board reconciliation=computed · Drawing ↔ schedule=computed. A dash / empty / unverifiable contracted cell FAILS its row — honest red beats fake green.
Full-size vector sheets: drawings/single-line-A1.pdf (sheet 1 of 1, ISO A1, lettering ≥2.5 mm) — see the Drawings register tab. Reading guide: read top-down from the utility incomer through the main board to each feeder; feeder tags and loads match the Panel schedule tab.
SG: Again seems a strange diagram everything connected to one line that doesn't really mean anything or show how they connect etc.
Convention: the schedule below is the single source for the electrical numbers on this tab. On the drawing, a ×N grouped circuit is labelled with its PER-UNIT current (the schedule's Design I is the whole circuit), and the LV system is stated at its 400 V nominal (a legacy '415 V' label names the same UK LV system). Where a drawing label and the schedule differ, the schedule governs.
⛔ 1 of 22 rows FAIL — single cause: board reference(s) absent from the single-line drawing: MAIN DISTRIBUTION BOARD (TP&N)
Fix route: route the electrical circuits in the scene (wire the electrical_bus edges) so route-manifest / connection-schedule carry real cable lengths, compute ΔU% = f(length, CSA, Design I) in draw_panel_schedule at source, and generate the single-line + schedule from the ONE distribution dataset so kVA / voltage / board names cannot diverge
MAIN DISTRIBUTION BOARD (TP&N)
Field | Value | Cell check
Board reference | Motor Control Center | PASS
Board type | Main distribution board | PASS
Supply source | Utility LV incomer (400 V distribution board) | PASS
System | 400 V 3-phase + N (TP&N) | PASS
Busbar rating | 100 A | PASS
Incoming feeder | 1.5 mm² · 5.4 m · ΔU 0.038% | PASS
Total connected load | 44.7 kW
Board demand (busbar) | 86 A | PASS
MAIN DISTRIBUTION BOARD (TP&N)
Ckt | Description | Ways | Conn. load (kW) | Design I (A) | Protective device | Cable (CSA · cores) | Length (m) | ΔU (%) | In spec | Row check | Audit: device rating (A) | Audit: Iz (A) — BS 7671 Method-C ampacity | Audit: check evidence (build-computed) | Audit: kW (parsed per-unit) | Audit: Design I (parsed) | Cell check
W1 | 3 Phase Power Input | 1 | 0.6 | 1.1 | 6 A MCB (sized) | 1.5 mm² · 3c+E | 5.7 | 0.041 | ✓ | PASS | 6 | 20 |  |  |  | PASS
W2 | Uv Disinfection | 1 | 4 | 7.5 | 10 A MCB (sized) | 1.5 mm² · 3c+E | 30.1 | 1.465 | ✓ | PASS | 10 | 20 |  |  |  | PASS
W3–4 | Fertigation Dosing Pump | 2 | 7.50 (×2=15.0) | 15.1 | 16 A MCB (sized) | 1.5 mm² · 3c+E | 8.7 | 0.85 | ✓ | PASS | 16 | 20 |  | 7.5 |  | PASS
W5 | Hand Watering Pump | 1 | 2.8 | 5.3 | 6 A MCB (sized) | 1.5 mm² · 3c+E | 36.5 | 1.255 | ✓ | PASS | 6 | 20 |  |  |  | PASS
W6–7 | Drain Transfer Pump | 2 | 1.92 (×2=3.8) | 3.8 | 6 A MCB (sized) | 1.5 mm² · 3c+E | 20.7 | 0.512 | ✓ | PASS | 6 | 20 |  | 1.92 |  | PASS
W8–9 | Cloth Filter | 2 | 0.60 (×2=1.2) | 1.1 | 6 A MCB (sized) | 1.5 mm² · 3c+E | 26.2 | 0.187 | ✓ | PASS | 6 | 20 |  | 0.6 |  | PASS
W10 | Irrigation / nutrient pump | 1 | 9.65 | 18.2 | 20 A MCB (sized) | 1.5 mm² · 3c+E | 33.2 | 3.931 | ✓ | PASS | 20 | 20 |  |  |  | PASS
W11 | Ro High Pressure Pump | 1 | 4.2 | 7.9 | 10 A MCB (sized) | 1.5 mm² · 3c+E | 37.6 | 1.931 | ✓ | PASS | 10 | 20 |  |  |  | PASS
W12 | Gac Filter | 1 | 0.6 | 1.1 | 6 A MCB (sized) | 1.5 mm² · 3c+E | 38.9 | 0.278 | ✓ | PASS | 6 | 20 |  |  |  | PASS
W13 | Permeate Outlet | 1 | 0.6 | 1.1 | 6 A MCB (sized) | 1.5 mm² · 3c+E | 24.5 | 0.175 | ✓ | PASS | 6 | 20 |  |  |  | PASS
W14 | Concentrate Outlet | 1 | 0.6 | 1.1 | 6 A MCB (sized) | 1.5 mm² · 3c+E | 21.5 | 0.154 | ✓ | PASS | 6 | 20 |  |  |  | PASS
W15 | Electrical Control Panel | 1 | 0.2 | 0.4 | 6 A MCB (sized) | 1.5 mm² · 3c+E | 7.5 | 0.02 | ✓ | PASS | 6 | 20 |  |  |  | PASS
W16 | Control + Instrument UPS | 1 | 0.5 | 0.9 | 6 A MCB (sized) | 1.5 mm² · 3c+E | 7.7 | 0.045 | ✓ | PASS | 6 | 20 |  |  |  | PASS
W17 | SCADA / Plant Control System | 1 | 0.5 | 0.9 | 6 A MCB (sized) | 1.5 mm² · 3c+E | 7.4 | 0.043 | ✓ | PASS | 6 | 20 |  |  |  | PASS
W18 | Electrical Control Cabinet | 1 | 0.2 | 0.4 | 6 A MCB (sized) | 1.5 mm² · 3c+E | 33.2 | 0.086 | ✓ | PASS | 6 | 20 |  |  |  | PASS
W19 | Digital Control Panel (control / aux feeder) | 1 | 0.2 | 0.4 | 6 A MCB (sized) | 1.5 mm² · 3c+E | 8 | 0.021 | ✓ | PASS | 6 | 20 |  |  |  | PASS
| TOTALS |  | 44.7 kW | 86 A
Main Switchboard
Field | Value | Cell check
Board reference | Main Switchboard | PASS
Board type | Sub-distribution board | PASS
Supply source | Local sub-distribution (MV feeder → local step-down transformer) | PASS
System | 400 V 3-phase + N (TP&N) | PASS
Busbar rating | 20 A | PASS
Incoming feeder | 1.5 mm² · 20.7 m · ΔU 0.147% | PASS
Total connected load | 9.7 kW
Board demand (busbar) | 18 A | PASS
Main Switchboard
Ckt | Description | Ways | Conn. load (kW) | Design I (A) | Protective device | Cable (CSA · cores) | Length (m) | ΔU (%) | In spec | Row check | Audit: device rating (A) | Audit: Iz (A) — BS 7671 Method-C ampacity | Audit: check evidence (build-computed) | Audit: kW (parsed per-unit) | Audit: Design I (parsed) | Cell check
W1 | Motor Control Center | 1 | 9.7 | 18.3 | 20 A MCB (sized) | 1.5 mm² · 3c+E | 5.4 | 0.645 | ✓ | PASS | 20 | 20 |  |  |  | PASS
| TOTALS |  | 9.7 kW | 18 A
Board & drawing reconciliation — contract checks (scored with the circuit rows above). These compare TWO ARTEFACTS (schedule ↔ single-line drawing ↔ contract): each side's value is EMBEDDED on the 'Audit data' sheet with its provenance, and the Row check is a live formula over those operand cells.
Check | Measured / compared | [7 empty] | Row check |  | Cell check
MAIN DISTRIBUTION BOARD (TP&N) · [board reconciliation] | Σ circuit design current 86 A vs busbar demand 86 A (ratio 1); busbar rating: 100 A | [7 empty] | PASS |  | PASS
Main Switchboard · [board reconciliation] | Σ circuit design current 18 A vs busbar demand 18 A (ratio 1); busbar rating: 20 A | [7 empty] | PASS |  | PASS
single-line ↔ schedule · system voltage | schedule system 400 V 3-phase; drawing voltages: 11000/400 V, 400 V | [7 empty] | PASS |  | PASS
single-line ↔ schedule · board hierarchy | schedule boards: MAIN DISTRIBUTION BOARD (TP&N), Main Switchboard | [7 empty] | FAIL — board reference(s) absent from the single-line drawing: MAIN DISTRIBUTION BOARD (TP&N) |  | PASS
single-line ↔ schedule · transformer kVA | drawing transformer 75.0 kVA vs contract quantity 75.0 kVA | [7 empty] | PASS |  | PASS

## Line & velocity
Line & velocity schedule | [11 empty] | ↑ Contents
⬤ TAB QUALITY 9.6/10 · PASS (target ≥8, live from the Quality & Audit score cell) · column-contract arithmetic: 10 × 68/71 rows passing; content checks: line & velocity column contract (per-row Row check) — cell completeness+type contract 497/497 · scor… · full audit: Quality & Audit tab
Every sized run, SPLIT so units never mix: process-pipe lines (flow, velocity vs the erosion band) · electrical & signal cables (current A, volt-drop band) · other services. Velocity is COMPUTED (the sizer's as-sized value when it carried a real flow, else v = Q ÷ A from the endpoint-matched contract flow over the sizer's DN bore); 'In spec' is the computed band comparison — never a default tick. Basis shows the flow/velocity derivation + how each Line £ is built. ROW CHECK CONTRACT (score = 10 × rows-passing ÷ rows = 10 × 68/71 = 9.6): Tag/From/To/Size=required_nonempty · Rating=computed · Velocity / ΔU=computed · Spec limit=required_nonempty · In spec=computed · Length (m)=required_nonempty · Line £ + Basis=required_nonempty. A dash / empty / unverifiable contracted cell FAILS its row — honest red beats fake green.
⛔ 3 of 71 rows FAIL — top causes: 2× velocity underivable — no flow demand on the edge and no contract flow/throughput quantity matches either endpoint; 1× no carried current on the run; ΔU% missing — volt-drop unverifiable (dash is never in-spec)
Fix route: author the real flow demand (required_value) on every fluid topology edge at source (universal-contract-sizing → connection ledger) so connection_sizing sizes bores from true flows; the schedule then carries computed velocities and the band check passes on the re-sized lines
Process pipe lines — flow (m³/s) · velocity limit ≤ 3 m/s
Basis note — common to the rows below (factored out of the per-row cells): cost model: model:uk-2026-supply+install
Tag | From | To | Size | Rating | Velocity / ΔU | Spec limit | Length (m) | In spec | Line £ | Basis | Row check | Audit: band | Audit: check evidence (build-computed) | Cell check
201-PR-DN65 | Gac Softener | Softener Vessel | DN65 | 14.5 m3/h | 1.304 | ≤3 m/s velocity | 7.79 | ✓ | 577.4 | DN65 pipe, 7.8 m, ΔP≈2.1 kPa · £60/m × 7.8 m · install £467 · as-sized by connection_sizing (post-upsize) from 14.5 m3/h | PASS | 3 |  | PASS
202-PR-DN125 | Gac Softener | Drain Collection Sump | DN125 | 45 m3/h | 0.968 | ≤3 m/s velocity | 10.84 | ✓ | 1669.2 | DN125 pipe, 10.8 m, ΔP≈0.7 kPa · £130/m × 10.8 m · install £1,409 · as-sized by connection_sizing (post-upsize) from 45 m3/h | PASS | 3 |  | PASS
203-PR-DN50 | Uf Module Bank | Ro High Pressure Pump | DN50 | 11 m3/h | 1.412 | ≤3 m/s velocity | 10.13 | ✓ | 570.24 | DN50 pipe, 10.1 m, ΔP≈3.9 kPa · £48/m × 10.1 m · install £486 · as-sized by connection_sizing (post-upsize) from 11 m3/h | PASS | 3 |  | PASS
204-PR-DN125 | Uf Module Bank | Drain Collection Sump | DN125 | 45 m3/h | 0.968 | ≤3 m/s velocity | 22.14 | ✓ | 3138.2 | DN125 pipe, 22.1 m, ΔP≈1.4 kPa · £130/m × 22.1 m · install £2,878 · as-sized by connection_sizing (post-upsize) from 45 m3/h | PASS | 3 |  | PASS
205-PR-DN50 | Ro High Pressure Pump | Reverse Osmosis Skid | DN50 | 11 m3/h | 1.412 | ≤3 m/s velocity | 27.89 | ✓ | 1422.72 | DN50 pipe, 27.9 m, ΔP≈10.8 kPa · £48/m × 27.9 m · install £1,339 · as-sized by connection_sizing (post-upsize) from 11 m3/h | PASS | 3 |  | PASS
206-PR-DN125 | Ro High Pressure Pump | Drain Collection Sump | DN125 | 45 m3/h | 0.968 | ≤3 m/s velocity | 32.13 | ✓ | 4436.9 | DN125 pipe, 32.1 m, ΔP≈2.1 kPa · £130/m × 32.1 m · install £4,177 · as-sized by connection_sizing (post-upsize) from 45 m3/h | PASS | 3 |  | PASS
207-PR-DN150 | Cloth Filter | Gac Filter | DN150 | 80 m3/h | 1.191 | ≤3 m/s velocity | 21.34 | ✓ | 3861.1 | DN150 pipe, 21.3 m, ΔP≈1.6 kPa · £165/m × 21.3 m · install £3,521 · as-sized by connection_sizing (post-upsize) from 80 m3/h | PASS | 3 |  | PASS
208-PR-DN125 | Cloth Filter | Drain Collection Sump | DN125 | 45 m3/h | 0.968 | ≤3 m/s velocity | 20.21 | ✓ | 2887.3 | DN125 pipe, 20.2 m, ΔP≈1.3 kPa · £130/m × 20.2 m · install £2,627 · as-sized by connection_sizing (post-upsize) from 45 m3/h | PASS | 3 |  | PASS
209-PR-DN150 | Gac Filter | Uv Disinfection | DN150 | 90 m3/h | 1.34 | ≤3 m/s velocity | 23.69 | ✓ | 4248.85 | DN150 pipe, 23.7 m, ΔP≈2.2 kPa · £165/m × 23.7 m · install £3,909 · as-sized by connection_sizing (post-upsize) from 90 m3/h | PASS | 3 |  | PASS
210-PR-DN125 | Gac Filter | Drain Collection Sump | DN125 | 45 m3/h | 0.968 | ≤3 m/s velocity | 29.59 | ✓ | 4106.7 | DN125 pipe, 29.6 m, ΔP≈1.9 kPa · £130/m × 29.6 m · install £3,847 · as-sized by connection_sizing (post-upsize) from 45 m3/h | PASS | 3 |  | PASS
211-PR-DN125 | Uv Disinfection | Drain Collection Sump | DN125 | 45 m3/h | 0.968 | ≤3 m/s velocity | 24.71 | ✓ | 3472.3 | DN125 pipe, 24.7 m, ΔP≈1.6 kPa · £130/m × 24.7 m · install £3,212 · as-sized by connection_sizing (post-upsize) from 45 m3/h | PASS | 3 |  | PASS
212-WT-DN125 | Drain Collection Sump | Drain Water Tank | DN125 | 45 m3/h | 0.968 | ≤3 m/s velocity | 11.74 | ✓ | 1786.2 | DN125 pipe, 11.7 m, ΔP≈0.8 kPa · £130/m × 11.7 m · install £1,526 · as-sized by connection_sizing (post-upsize) from 45 m3/h | PASS | 3 |  | PASS
213-PR-DN150 | Drain Collection Sump | Uv Disinfection | DN150 | 90 m3/h | 1.34 | ≤3 m/s velocity | 19.39 | ✓ | 3539.35 | DN150 pipe, 19.4 m, ΔP≈1.8 kPa · £165/m × 19.4 m · install £3,199 · as-sized by connection_sizing (post-upsize) from 90 m3/h | PASS | 3 |  | PASS
214-WT-DN80 | Drain Collection Sump | Hand Watering Pump | DN80 | 25 m3/h | 1.457 | ≤3 m/s velocity | 26.16 | ✓ | 2075.84 | DN80 pipe, 26.2 m, ΔP≈6.6 kPa · £74/m × 26.2 m · install £1,936 · as-sized by connection_sizing (post-upsize) from 25 m3/h | PASS | 3 |  | PASS
215-PR-DN150 | Drain Collection Sump | Cloth Filter | DN150 | 80 m3/h | 1.191 | ≤3 m/s velocity | 10 | ✓ | 1990 | DN150 pipe, 10.0 m, ΔP≈0.8 kPa · £165/m × 10.0 m · install £1,650 · as-sized by connection_sizing (post-upsize) from 80 m3/h | PASS | 3 |  | PASS
216-PR-DN65 | Drain Collection Sump | Gac Softener | DN65 | 14.5 m3/h | 1.304 | ≤3 m/s velocity | 6.17 | ✓ | 480.2 | DN65 pipe, 6.2 m, ΔP≈1.7 kPa · £60/m × 6.2 m · install £370 · as-sized by connection_sizing (post-upsize) from 14.5 m3/h | PASS | 3 |  | PASS
217-PR-DN150 | Drain Collection Sump | Irrigation Pump | DN150 | 90 m3/h | 1.34 | ≤3 m/s velocity | 23.46 | ✓ | 4210.9 | DN150 pipe, 23.5 m, ΔP≈2.2 kPa · £165/m × 23.5 m · install £3,871 · as-sized by connection_sizing (post-upsize) from 90 m3/h | PASS | 3 |  | PASS
218-PR-DN125 | Drain Collection Sump | Reverse Osmosis Skid | DN125 | 45 m3/h | 0.968 | ≤3 m/s velocity | 4.83 | ✓ | 887.9 | DN125 pipe, 4.8 m, ΔP≈0.3 kPa · £130/m × 4.8 m · install £628 · as-sized by connection_sizing (post-upsize) from 45 m3/h | PASS | 3 |  | PASS
219-PR-DN50 | Drain Collection Sump | Ro High Pressure Pump | DN50 | 11 m3/h | 1.412 | ≤3 m/s velocity | 27.2 | ✓ | 1389.6 | DN50 pipe, 27.2 m, ΔP≈10.5 kPa · £48/m × 27.2 m · install £1,306 · as-sized by connection_sizing (post-upsize) from 11 m3/h | PASS | 3 |  | PASS
220-PR-DN65 | Drain Collection Sump | Gac Filter | DN65 | 14.5 m3/h | 1.304 | ≤3 m/s velocity | 23.75 | ✓ | 1535 | DN65 pipe, 23.8 m, ΔP≈6.4 kPa · £60/m × 23.8 m · install £1,425 · as-sized by connection_sizing (post-upsize) from 14.5 m3/h | PASS | 3 |  | PASS
221-PR-DN125 | Drain Collection Sump | Uf Module Bank | DN125 | 45 m3/h | 0.968 | ≤3 m/s velocity | 8.37 | ✓ | 1348.1 | DN125 pipe, 8.4 m, ΔP≈0.5 kPa · £130/m × 8.4 m · install £1,088 · as-sized by connection_sizing (post-upsize) from 45 m3/h | PASS | 3 |  | PASS
222-PR-DN32 | Drain Collection Sump | Cip Tank | DN32 | 4 m3/h | 1.148 | ≤3 m/s velocity | 20.09 | ✓ | 735.06 | DN32 pipe, 20.1 m, ΔP≈8.8 kPa · £34/m × 20.1 m · install £683 · as-sized by connection_sizing (post-upsize) from 4 m3/h | PASS | 3 |  | PASS
223-PR-DN32 | Drain Collection Sump | Cip Tank | DN32 | 4 m3/h | 1.148 | ≤3 m/s velocity | 23.71 | ✓ | 858.14 | DN32 pipe, 23.7 m, ΔP≈10.4 kPa · £34/m × 23.7 m · install £806 · as-sized by connection_sizing (post-upsize) from 4 m3/h | PASS | 3 |  | PASS
224-WT-DN125 | Drain Water Tank | Drain Transfer Pump | DN125 | 45 m3/h | 0.968 | ≤3 m/s velocity | 33.1 | ✓ | 4563 | DN125 pipe, 33.1 m, ΔP≈2.2 kPa · £130/m × 33.1 m · install £4,303 · as-sized by connection_sizing (post-upsize) from 45 m3/h | PASS | 3 |  | PASS
225-PR-DN32 | Drain Transfer Pump | Cip Tank | DN32 | 4 m3/h | 1.148 | ≤3 m/s velocity | 45.21 | ✓ | 1589.14 | DN32 pipe, 45.2 m, ΔP≈19.7 kPa · £34/m × 45.2 m · install £1,537 · as-sized by connection_sizing (post-upsize) from 4 m3/h | PASS | 3 |  | PASS
226-PR-DN32 | Cip Tank | Cip Tank | DN32 | 4 m3/h | 1.148 | ≤3 m/s velocity | 3.11 | ✓ | 157.74 | DN32 pipe, 3.1 m, ΔP≈1.4 kPa · £34/m × 3.1 m · install £106 · as-sized by connection_sizing (post-upsize) from 4 m3/h | PASS | 3 |  | PASS
227-PR-DN125 | Cip Tank | Drain Collection Sump | DN125 | 45 m3/h | 0.968 | ≤3 m/s velocity | 20.42 | ✓ | 2914.6 | DN125 pipe, 20.4 m, ΔP≈1.3 kPa · £130/m × 20.4 m · install £2,655 · as-sized by connection_sizing (post-upsize) from 45 m3/h | PASS | 3 |  | PASS
228-WT-DN32 | Cip Tank | Fresh Water Tank | DN32 | 4 m3/h | 1.148 | ≤3 m/s velocity | 13.66 | ✓ | 516.44 | DN32 pipe, 13.7 m, ΔP≈6.0 kPa · £34/m × 13.7 m · install £464 · as-sized by connection_sizing (post-upsize) from 4 m3/h | PASS | 3 |  | PASS
229-PR-DN125 | Cip Tank | Drain Collection Sump | DN125 | 45 m3/h | 0.968 | ≤3 m/s velocity | 24.26 | ✓ | 3413.8 | DN125 pipe, 24.3 m, ΔP≈1.6 kPa · £130/m × 24.3 m · install £3,154 · as-sized by connection_sizing (post-upsize) from 45 m3/h | PASS | 3 |  | PASS
230-WT-DN25 | Fresh Water Tank | Nutrient Tank | DN25 (nominal — flow unknown) | — | UNVERIFIED | ≤3 m/s velocity (UNVERIFIED — no flow demand) | 5 | ✗ | 180 | DN25 nominal pipe, 5.0 m (flow unknown) · £28/m × 5.0 m · install £140 | FAIL — velocity underivable — no flow demand on the edge and no contract flow/throughput quantity matches either endpoint |  | velocity underivable — no flow demand on the edge and no contract flow/throughput quantity matches either endpoint | PASS
231-WT-DN150 | Fresh Water Tank | Permeate Outlet | DN150 | 90 m3/h | 1.34 | ≤3 m/s velocity | 30.62 | ✓ | 3235.38 | DN150 pipe, 30.6 m, ΔP≈2.9 kPa · £99/m × 30.6 m · install £3,031 · as-sized by connection_sizing (post-upsize) from 90 m3/h | PASS | 3 |  | PASS
232-WT-DN65 | Fresh Water Tank | Softener Vessel | DN65 | 14.5 m3/h | 1.304 | ≤3 m/s velocity | 31.14 | ✓ | 1978.4 | DN65 pipe, 31.1 m, ΔP≈8.4 kPa · £60/m × 31.1 m · install £1,868 · as-sized by connection_sizing (post-upsize) from 14.5 m3/h | PASS | 3 |  | PASS
233-WT-DN125 | Fresh Water Tank | Drain Collection Sump | DN125 | 45 m3/h | 0.968 | ≤3 m/s velocity | 27.23 | ✓ | 3799.9 | DN125 pipe, 27.2 m, ΔP≈1.8 kPa · £130/m × 27.2 m · install £3,540 · as-sized by connection_sizing (post-upsize) from 45 m3/h | PASS | 3 |  | PASS
234-WT-DN125 | Fresh Water Tank | Drain Transfer Pump | DN125 | 45 m3/h | 0.968 | ≤3 m/s velocity | 25.4 | ✓ | 3562 | DN125 pipe, 25.4 m, ΔP≈1.7 kPa · £130/m × 25.4 m · install £3,302 · as-sized by connection_sizing (post-upsize) from 45 m3/h | PASS | 3 |  | PASS
235-WT-DN25 | Fresh Water Tank | Drain Water Tank | DN25 (nominal — flow unknown) | — | UNVERIFIED | ≤3 m/s velocity (UNVERIFIED — no flow demand) | 19.98 | ✗ | 599.44 | DN25 nominal pipe, 20.0 m (flow unknown) · £28/m × 20.0 m · install £559 | FAIL — velocity underivable — no flow demand on the edge and no contract flow/throughput quantity matches either endpoint |  | velocity underivable — no flow demand on the edge and no contract flow/throughput quantity matches either endpoint | PASS
236-WT-DN80 | Fertigation Dosing Pump | Hand Watering Pump | DN80 | 25 m3/h | 1.457 | ≤3 m/s velocity | 30.23 | ✓ | 2377.02 | DN80 pipe, 30.2 m, ΔP≈7.6 kPa · £74/m × 30.2 m · install £2,237 · as-sized by connection_sizing (post-upsize) from 25 m3/h | PASS | 3 |  | PASS
237-PR-DN125 | Fertigation Dosing Pump | Drain Collection Sump | DN125 | 45 m3/h | 0.968 | ≤3 m/s velocity | 15.77 | ✓ | 2310.1 | DN125 pipe, 15.8 m, ΔP≈1.0 kPa · £130/m × 15.8 m · install £2,050 · as-sized by connection_sizing (post-upsize) from 45 m3/h | PASS | 3 |  | PASS
238-WT-DN150 | Hand Watering Pump | Irrigation Pump | DN150 | 90 m3/h | 1.34 | ≤3 m/s velocity | 6.54 | ✓ | 1419.1 | DN150 pipe, 6.5 m, ΔP≈0.6 kPa · £165/m × 6.5 m · install £1,079 · as-sized by connection_sizing (post-upsize) from 90 m3/h | PASS | 3 |  | PASS
239-WT-DN125 | Hand Watering Pump | Drain Collection Sump | DN125 | 45 m3/h | 0.968 | ≤3 m/s velocity | 30.5 | ✓ | 4225 | DN125 pipe, 30.5 m, ΔP≈2.0 kPa · £130/m × 30.5 m · install £3,965 · as-sized by connection_sizing (post-upsize) from 45 m3/h | PASS | 3 |  | PASS
240-PR-DN125 | Irrigation Pump | Distribution Manifold | DN125 | 45 m3/h | 0.968 | ≤3 m/s velocity | 1.87 | ✓ | 503.1 | DN125 pipe, 1.9 m, ΔP≈0.1 kPa · £130/m × 1.9 m · install £243 · as-sized by connection_sizing (post-upsize) from 45 m3/h | PASS | 3 |  | PASS
241-PR-DN125 | Irrigation Pump | Drain Collection Sump | DN125 | 45 m3/h | 0.968 | ≤3 m/s velocity | 28.06 | ✓ | 3907.8 | DN125 pipe, 28.1 m, ΔP≈1.8 kPa · £130/m × 28.1 m · install £3,648 · as-sized by connection_sizing (post-upsize) from 45 m3/h | PASS | 3 |  | PASS
242-WT-DN20 | Ultrafiltration Module | Fresh Water Tank | DN20 | 1.35 m3/h | 1.083 | ≤3 m/s velocity | 20.6 | ✓ | 291.12 | DN20 pipe, 20.6 m, ΔP≈15.4 kPa · £13/m × 20.6 m · install £272 · as-sized by connection_sizing (post-upsize) from 1.35 m3/h | PASS | 3 |  | PASS
243-PR-DN32 | Permeate Outlet | Cip Tank | DN32 | 4 m3/h | 1.148 | ≤3 m/s velocity | 50.87 | ✓ | 1781.58 | DN32 pipe, 50.9 m, ΔP≈22.2 kPa · £34/m × 50.9 m · install £1,730 · as-sized by connection_sizing (post-upsize) from 4 m3/h | PASS | 3 |  | PASS
244-PR-DN65 | Softener Vessel | Ultrafiltration Module | DN65 | 14.5 m3/h | 1.304 | ≤3 m/s velocity | 25.44 | ✓ | 1636.4 | DN65 pipe, 25.4 m, ΔP≈6.8 kPa · £60/m × 25.4 m · install £1,526 · as-sized by connection_sizing (post-upsize) from 14.5 m3/h | PASS | 3 |  | PASS
245-PR-DN125 | Nutrient Tank | Drain Collection Sump | DN125 | 45 m3/h | 0.968 | ≤3 m/s velocity | 31.38 | ✓ | 4339.4 | DN125 pipe, 31.4 m, ΔP≈2.0 kPa · £130/m × 31.4 m · install £4,079 · as-sized by connection_sizing (post-upsize) from 45 m3/h | PASS | 3 |  | PASS
246-PR-DN125 | Distribution Manifold | Drain Collection Sump | DN125 | 45 m3/h | 0.968 | ≤3 m/s velocity | 29.39 | ✓ | 4080.7 | DN125 pipe, 29.4 m, ΔP≈1.9 kPa · £130/m × 29.4 m · install £3,821 · as-sized by connection_sizing (post-upsize) from 45 m3/h | PASS | 3 |  | PASS
247-PR-DN125 | Reverse Osmosis Skid | Drain Collection Sump | DN125 | 45 m3/h | 0.968 | ≤3 m/s velocity | 11.62 | ✓ | 1770.6 | DN125 pipe, 11.6 m, ΔP≈0.8 kPa · £130/m × 11.6 m · install £1,511 · as-sized by connection_sizing (post-upsize) from 45 m3/h | PASS | 3 |  | PASS
| Σ Process pipe lines | [7 empty] | 106378.96
Electrical & signal cables — current (A) · volt-drop limit ≤ 5 %
Basis note — common to the rows below (factored out of the per-row cells): cost model: model:uk-2026-supply+install
Tag | From | To | Size | Rating | Velocity / ΔU | Spec limit | Length (m) | In spec | Line £ | Basis | Row check | Audit: band | Audit: check evidence (build-computed) | Cell check
242-WT-DN20 | Mains Incomer | Standby Diesel Generator | 1.5 mm² | 4.2 A | 0.068 | ≤5% volt-drop | 9.61 | ✓ | 40.83 | 1 × 1.5 mm² Cu, 9.6 m · £3/m × 9.6 m · install £29 · volt-drop at 4.2 A over 9.61 m | PASS | 5 |  | PASS
243-PR-DN32 | Standby Diesel Generator | Distribution Transformer | 1.5 mm² | 4.2 A | 0.057 | ≤5% volt-drop | 8.01 | ✓ | 36.03 | 1 × 1.5 mm² Cu, 8.0 m · £3/m × 8.0 m · install £24 · volt-drop at 4.2 A over 8.01 m | PASS | 5 |  | PASS
244-PR-DN65 | Distribution Transformer | Main Switchboard | 1.5 mm² | 4.2 A | 0.147 | ≤5% volt-drop | 20.72 | ✓ | 74.16 | 1 × 1.5 mm² Cu, 20.7 m · £3/m × 20.7 m · install £62 · volt-drop at 4.2 A over 20.72 m | PASS | 5 |  | PASS
245-PR-DN125 | Main Switchboard | Motor Control Center | 1.5 mm² | 4.2 A | 0.038 | ≤5% volt-drop | 5.43 | ✓ | 28.29 | 1 × 1.5 mm² Cu, 5.4 m · £3/m × 5.4 m · install £16 · volt-drop at 4.2 A over 5.43 m | PASS | 5 |  | PASS
246-PR-DN125 | Motor Control Center | Electrical Control Panel | 1.5 mm² | 4.2 A | 0.155 | ≤5% volt-drop | 6.07 | ✓ | 30.21 | 1 × 1.5 mm² Cu, 6.1 m · £3/m × 6.1 m · install £18 · volt-drop at 4.2 A over 6.07 m | PASS | 5 |  | PASS
247-PR-DN125 | Motor Control Center | 3 Phase Power Input | 1.5 mm² | 4.2 A | 0.147 | ≤5% volt-drop | 5.73 | ✓ | 29.19 | 1 × 1.5 mm² Cu, 5.7 m · £3/m × 5.7 m · install £17 · volt-drop at 4.2 A over 5.73 m | PASS | 5 |  | PASS
48 | Motor Control Center | Control + Instrument UPS | 1.5 mm² | 4.2 A | 0.147 | ≤5% volt-drop | 5.72 | ✓ | 29.16 | 1 × 1.5 mm² Cu, 5.7 m · £3/m × 5.7 m · install £17 · volt-drop at 4.2 A over 5.72 m | PASS | 5 |  | PASS
49 | Motor Control Center | SCADA / Plant Control System | 1.5 mm² | 4.2 A | 0.16 | ≤5% volt-drop | 6.26 | ✓ | 30.78 | 1 × 1.5 mm² Cu, 6.3 m · £3/m × 6.3 m · install £19 · volt-drop at 4.2 A over 6.26 m | PASS | 5 |  | PASS
50 | Motor Control Center | Uv Disinfection | 1.5 mm² | 8.2 A | 1.345 | ≤5% volt-drop | 27.07 | ✓ | 93.21 | 1 × 1.5 mm² Cu, 27.1 m · £3/m × 27.1 m · install £81 · volt-drop at 8.2 A over 27.07 m | PASS | 5 |  | PASS
51 | Motor Control Center | Fertigation Dosing Pump | 1.5 mm² | 15 A | 1.874 | ≤5% volt-drop | 20.74 | ✓ | 74.22 | 1 × 1.5 mm² Cu, 20.7 m · £3/m × 20.7 m · install £62 · volt-drop at 15 A over 20.74 m | PASS | 5 |  | PASS
52 | Motor Control Center | Hand Watering Pump | 1.5 mm² | 4.2 A | 0.856 | ≤5% volt-drop | 33.45 | ✓ | 112.35 | 1 × 1.5 mm² Cu, 33.4 m · £3/m × 33.5 m · install £100 · volt-drop at 4.2 A over 33.45 m | PASS | 5 |  | PASS
53 | Motor Control Center | Drain Transfer Pump | 1.5 mm² | 3.9 A | 0.87 | ≤5% volt-drop | 37.27 | ✓ | 123.81 | 1 × 1.5 mm² Cu, 37.3 m · £3/m × 37.3 m · install £112 · volt-drop at 3.9 A over 37.27 m | PASS | 5 |  | PASS
54 | Motor Control Center | Cloth Filter | 1.5 mm² | 4.2 A | 0.594 | ≤5% volt-drop | 23.22 | ✓ | 81.66 | 1 × 1.5 mm² Cu, 23.2 m · £3/m × 23.2 m · install £70 · volt-drop at 4.2 A over 23.22 m | PASS | 5 |  | PASS
55 | Motor Control Center | Irrigation Pump | 1.5 mm² | 4.2 A | 0.774 | ≤5% volt-drop | 30.25 | ✓ | 102.75 | 1 × 1.5 mm² Cu, 30.2 m · £3/m × 30.2 m · install £91 · volt-drop at 4.2 A over 30.25 m | PASS | 5 |  | PASS
56 | Motor Control Center | Ro High Pressure Pump | 1.5 mm² | 8.4 A | 1.747 | ≤5% volt-drop | 34.63 | ✓ | 115.89 | 1 × 1.5 mm² Cu, 34.6 m · £3/m × 34.6 m · install £104 · volt-drop at 8.4 A over 34.63 m | PASS | 5 |  | PASS
57 | Motor Control Center | Gac Filter | 1.5 mm² | 4.2 A | 0.995 | ≤5% volt-drop | 38.88 | ✓ | 128.64 | 1 × 1.5 mm² Cu, 38.9 m · £3/m × 38.9 m · install £117 · volt-drop at 4.2 A over 38.88 m | PASS | 5 |  | PASS
58 | Motor Control Center | Permeate Outlet | 1.5 mm² | 4.2 A | 0.627 | ≤5% volt-drop | 24.51 | ✓ | 85.53 | 1 × 1.5 mm² Cu, 24.5 m · £3/m × 24.5 m · install £74 · volt-drop at 4.2 A over 24.51 m | PASS | 5 |  | PASS
59 | Motor Control Center | Concentrate Outlet | 1.5 mm² | 4.2 A | 0.551 | ≤5% volt-drop | 21.51 | ✓ | 76.53 | 1 × 1.5 mm² Cu, 21.5 m · £3/m × 21.5 m · install £65 · volt-drop at 4.2 A over 21.51 m | PASS | 5 |  | PASS
60 | Motor Control Center | Electrical Control Cabinet | 1.5 mm² | 4.2 A | 0.85 | ≤5% volt-drop | 33.22 | ✓ | 111.66 | 1 × 1.5 mm² Cu, 33.2 m · £3/m × 33.2 m · install £100 · volt-drop at 4.2 A over 33.22 m | PASS | 5 |  | PASS
61 | Motor Control Center | Digital Control Panel | (unsized — no design current) | — | UNVERIFIED | ≤5% volt-drop (UNVERIFIED — no design current) | 28.09 | ✗ | 96.27 | power feeder, 28.1 m (design current unknown) · £3/m × 28.1 m · install £84 | FAIL — no carried current on the run; ΔU% missing — volt-drop unverifiable (dash is never in-spec) |  | no carried current on the run; ΔU% missing — volt-drop unverifiable (dash is never in-spec) | PASS
62 | Electrical Control Panel | Digital Control Panel | 1.5 mm² | 0.5 A | 0.098 | ≤5% volt-drop | 31.49 | ✓ | 106.47 | 1 × 1.5 mm² Cu, 31.5 m · £3/m × 31.5 m · install £94 · volt-drop at 0.5 A over 31.49 m | PASS | 5 |  | PASS
63 | Control + Instrument UPS | Digital Control Panel | 1.5 mm² | 0.5 A | 0.079 | ≤5% volt-drop | 25.37 | ✓ | 88.11 | 1 × 1.5 mm² Cu, 25.4 m · £3/m × 25.4 m · install £76 · volt-drop at 0.5 A over 25.37 m | PASS | 5 |  | PASS
64 | Motor Control Center | Digital Control Panel | 1.5 mm² | 0.5 A | 0.086 | ≤5% volt-drop | 27.48 | ✓ | 94.44 | 1 × 1.5 mm² Cu, 27.5 m · £3/m × 27.5 m · install £82 · volt-drop at 0.5 A over 27.48 m | PASS | 5 |  | PASS
66 | Electrical Control Cabinet | Digital Control Panel | 1.5 mm² | 0.5 A | 0.091 | ≤5% volt-drop | 29.06 | ✓ | 99.18 | 1 × 1.5 mm² Cu, 29.1 m · £3/m × 29.1 m · install £87 · volt-drop at 0.5 A over 29.06 m | PASS | 5 |  | PASS
| Σ Electrical & signal cables | [7 empty] | 1889.37
| Rows FAILING the column contract (all sections, live count) | [6 empty] | 3

## Assembly sequence
Assembly & erection sequence — derived from this design | [7 empty] | ↑ Contents
⬤ TAB QUALITY 10/10 · PASS (target ≥8, live from the Quality & Audit score cell) · arithmetic: 10 × min(steps 13/13, heavy-lift callouts 1/1, programme reconciliation 1/1); content checks: design-derived step arithmetic — steps with design-derived dura… · full audit: Quality & Audit tab
Order of works DERIVED FROM THE DESIGN: civils sized from the placed-plant footprint, one erection step per process region (GA order) with equipment grouped by module, pipework/electrical quantified from the connection schedule, and durations from the group counts × the unit norms footnoted below (ESTIMATE). Hold / witness points gate each step. A site-specific construction phase plan (CDM) is still required before works begin.
LARGEST LIFT: Fresh Water Tank [TK-108] at 656 kg (heaviest vessel mass in the bill of materials) → 20 t mobile crane (or lorry-mounted HIAB). Rule (ESTIMATE): crane rated ≥5× the load at a ~10 m working radius.
Heavy lifts (>1 t): none — no BoM item exceeds 1,000 kg, so there is no further lift plant to call out beyond the largest-lift line above.
Step | Phase / activity | Scope — equipment groups (tags) | Predecessor | Lifting plant | Duration | Days (live) | Hold / witness point | Cell check
1 | Site set-out & civils | Ground-bearing slab 22.8 × 26.6 m (606.2 m², from the placed-plant footprint) + plinths, bunds & drainage falls | Site handover | Excavator, concrete pump | ~15.5 crew-days (ESTIMATE) | 15.16 | Set-out survey + concrete cube tests signed off | PASS | SG: Initial page suggested almost no civils cost?
2 | Erect & set — Maintenance serviceability | Cip Tank TK-101; Cleaning Tank TK-102 | Civils complete & cured | 20 t mobile crane (or lorry-mounted HIAB) | ~1 crew-day (ESTIMATE) | 0.67 | Vessel hydrostatic (leak) test witnessed; machines: alignment + rotation (bump) test | PASS
3 | Erect & set — Mass fluid transport process | 8× Nutrient Tank TK-103, TK-104, TK-105, TK-109 (+4 more) — see GA; 2× Cloth Filter V-104, V-105; 2× Drain Collection Sump TK-114, TK-115; 2× Drain Transfer Pump P-103, P-104; 2× Drain Water Tank TK-106, TK-107; 2× Fertigation Dosing Pump P-106, P-107; 2× Softener Vessel V-106, V-107; Distribution Manifold M-101; Fresh Water Tank TK-108; Gac Filter V-101; (+8 more groups, 8 items — see GA) | Erect & set — Maintenance serviceability set | 20 t mobile crane (or lorry-mounted HIAB) | ~9.5 crew-days (ESTIMATE) | 9.42 | Vessel hydrostatic (leak) test witnessed; machines: alignment + rotation (bump) test | PASS
4 | Erect & set — Structure containment | Transformer TX-101 | Erect & set — Mass fluid transport process set | Forklift / pallet truck | ~0.5 crew-days (ESTIMATE) | 0.5 | Alignment + rotation (bump) test recorded | PASS
5 | Erect & set — Energy storage source | Main Switchboard EP-101; Mains Incomer EP-102 | Erect & set — Structure containment set | Forklift / pallet truck | ~0.5 crew-days (ESTIMATE) | 0.5 | Alignment + rotation (bump) test recorded | PASS
6 | Erect & set — Environmental interface | Concentrate Outlet X-103; Permeate Outlet X-104 | Erect & set — Energy storage source set | Forklift / pallet truck | ~0.5 crew-days (ESTIMATE) | 0.5 | Alignment + rotation (bump) test recorded | PASS
7 | Erect & set — Power distribution | 3 Phase Power Input D-101; Control + Instrument UPS U-201; Distribution Transformer TX-102; Electrical Control Panel X-102; Motor Control Center EP-104; SCADA / Plant Control System EP-103; Standby Diesel Generator G-201 | Erect & set — Environmental interface set | Forklift / pallet truck | ~2 crew-days (ESTIMATE) | 1.75 | Alignment + rotation (bump) test recorded | PASS
8 | Erect & set — Control compute communication | Digital Control Panel I-103 | Erect & set — Power distribution set | Forklift / pallet truck | ~0.5 crew-days (ESTIMATE) | 0.5 | Alignment + rotation (bump) test recorded | PASS
9 | Erect & set — Safety protection | Electrical Control Cabinet I-102 | Erect & set — Control compute communication set | Forklift / pallet truck | ~0.5 crew-days (ESTIMATE) | 0.5 | Alignment + rotation (bump) test recorded | PASS
10 | Pipework & interconnections | 996.7 m of sized pipe across 71 runs (DN125 443.6 m, DN150 135 m, DN20 20.6 m, DN25 (nominal — flow unknown) 25 m, DN32 156.6 m, DN50 65.2 m) — per the connection schedule / Line & velocity tab | Equipment set & grouted | Pipe trolleys, chain hoists | ~40 crew-days (ESTIMATE) | 39.87 | Pressure / leak test certificate per line | PASS
11 | Electrical installation | 533.8 m of LV cable per the connection schedule; boards & distribution per the Electrical tab (single-line + panel schedule) | Cable routes / trays installed | Cable drum jacks | ~9 crew-days (ESTIMATE) | 8.9 | Insulation-resistance + earth-continuity tests | PASS
12 | Instrumentation, controls & SCADA | 51 instrument loop(s) from the bill of materials — mount, hook-up, loop-check | Electrical energised (LV) | Hand tools | ~6.5 crew-days (ESTIMATE) | 6.38 | Loop checks + calibration certificates | PASS
13 | Pre-commissioning & commissioning | Whole plant — flush, fill, leak-check, energise, wet-commission, performance test (47 principal items) | All systems installed & tested | — | ~10 crew-days (ESTIMATE) | 9.7 | Water-on, functional + performance test; client witness | PASS
​="Critical-path total (serial programme): "&TEXT(SUM($G$9:$G$21),"0.0")&" crew-day(s) (ESTIMATE norms, footnoted below) — reconciliation: no independent construction-programme duration exists elsewhere in this dossier (checked: Cost waterfall, Financial model) to compare against; nothing diverges"
Duration norms used above — stated, industry-plausible defaults (ESTIMATE, not design-derived)
| civils: 40 m² slab per crew-day | ESTIMATE — ground-bearing slab + plinths/bunds, incl. set-out & cure wait overlap
| vessel: 3 vessel lifts per crane-day | ESTIMATE — set, level, grout & hold — light vessels (<5 t) on a mobile crane
| machine: 4 items per crew-day | ESTIMATE — skid/machine set + alignment on prepared plinths
| pipe: 25 m installed & tested per crew-day | ESTIMATE — carbon/PE process pipe incl. supports, per 2-fitter crew
| cable: 60 m pulled & terminated per crew-day | ESTIMATE — LV power/control cable on tray, per 2-electrician crew
| loop: 8 instrument loops per crew-day | ESTIMATE — mount, hook-up, loop-check & calibration certificate
| commission: 10 principal items per day + 5 days flat | ESTIMATE — flush/fill/leak-check, energise, wet-commission, performance test

## Risk & Regulatory
Risk & Regulatory | [12 empty] | ↑ Contents
⬤ TAB QUALITY 10/10 · PASS (target ≥8, live from the Quality & Audit score cell) · column-contract arithmetic: 10 × 8/8 rows passing; content checks: risk-register column contract (per-row triage) — cell completeness+type contract 176/176 · score = min… · full audit: Quality & Audit tab
Preliminary hazard & risk register PLUS the regulatory / compliance duties, on one sheet (both derive from the same universal hazard library). Risk rows come LIVE from the physics critic (CORROBORATED findings only — an uncorroborated critic note is never a hazard; see 'Engine advisories' below), the deterministic gate flags, the cost-sanity check and the equipment present; the regulatory section adds the engine's compliance-gate verdict and the jurisdiction × hazard → regulation matrix. Score = S × L (≤7 Low / 8–14 Medium / ≥15 High). Every row is TRIAGED from its own provenance + content: an ENGINE-FIXABLE row (a design defect the engine controls — sizing / spec / coverage / consistency) is an OPEN DEFECT that names its routed fix stage and can never ship as 'tolerable with mitigation'; only a genuinely EXTERNAL risk (inherent process hazard, site / utility / supply-chain / regulatory factor) carries a mitigation. Universal — not plant-specific. Preliminary; a site-specific HAZID / HAZOP and a regulatory review are required before construction / sale. TAB SCORE = register structure & completeness, not a claim of 'no risk' — read the register summary below the 'Risk register' heading. ROW CHECK CONTRACT (score = 10 × rows-passing ÷ rows = 10 × 8/8 = 10.0): Class=computed · Mitigation / fix route=required_nonempty · Residual=computed. A dash / empty / unverifiable contracted cell FAILS its row — honest red beats fake green.
Risk register
Register summary: 8 genuine hazard(s) in this register — 0 High / 6 Medium / 2 Low — plus 4 uncorroborated engine advisory(ies) listed separately in 'Engine advisories' below (NOT counted as hazards, no severity/likelihood scoring). The 'TAB QUALITY' score above this register measures structure & completeness of the triage, never the absence of risk.
# | Category | Hazard / finding | Cause | S | L | Score | Rating | Class | Mitigation / fix route | Residual | Source | Row check | Audit: check evidence (build-computed triage) | Cell check
1 | Process safety / HSE | Toxic / asphyxiant gas release | Biological or chemical processes can release ammonia, hydrogen sulphide or chlorine. | 4 | 2 | 8 | Medium | EXTERNAL | Gas detection, forced ventilation, scrubbing, respiratory PPE, confined-space controls. | Tolerable (with mitigation) | Equipment present in the bill of materials | PASS |  | PASS
2 | Process safety / HSE | Stored pressure energy | Pressurised vessels and lines can fail explosively. | 4 | 2 | 8 | Medium | EXTERNAL | Design + periodic inspection to pressure code, relief devices, written scheme of examination. | Tolerable (with mitigation) | Equipment present in the bill of materials | PASS |  | PASS
3 | Process safety / HSE | Rotating machinery — entanglement / mechanical failure | Exposed rotating parts; stored mechanical energy; loss of a duty machine upsets the process. | 3 | 3 | 9 | Medium | EXTERNAL | Fixed guarding, lock-off / isolation (LOTO), N+1 standby on critical duties, vibration monitoring. | Tolerable (with mitigation) | Equipment present in the bill of materials | PASS |  | PASS
4 | Process safety / HSE | Electrical — shock / arc-flash | High fault energy at switchgear and transformers; shock risk from LV / HV. | 4 | 2 | 8 | Medium | EXTERNAL | BS 7671 installation, arc-flash assessment, lock-off, IP-rated enclosures, RCD + earthing. | Tolerable (with mitigation) | Equipment present in the bill of materials | PASS |  | PASS
5 | Process safety / HSE | Working at height / confined space (tanks & vessels) | Tank tops present a fall risk; tank interiors are confined spaces (atmosphere / drowning). | 4 | 2 | 8 | Medium | EXTERNAL | Edge protection, confined-space permit-to-work, atmosphere testing, rescue plan. | Tolerable (with mitigation) | Equipment present in the bill of materials | PASS |  | PASS
6 | Process safety / HSE | Environmental discharge to controlled waters | Process effluent or sludge discharged to controlled waters requires consent. | 3 | 3 | 9 | Medium | EXTERNAL | Discharge permit, effluent treatment to consent limits, monitoring + reporting. | Tolerable (with mitigation) | Equipment present in the bill of materials | PASS |  | PASS
7 | Process safety / HSE | Chemical handling — corrosive / reactive | Dosing chemicals are corrosive or reactive; incompatible mixing is hazardous. | 3 | 2 | 6 | Low | EXTERNAL | Bunding, segregated storage, COSHH assessment, PPE, eyewash / safety shower. | Tolerable (with mitigation) | Equipment present in the bill of materials | PASS |  | PASS
8 | Process safety / HSE | Radiation — ultraviolet / ozone exposure | Ultraviolet reactors emit harmful UV; ozone is a respiratory irritant. | 2 | 2 | 4 | Low | EXTERNAL | Interlocked enclosures, UV-opaque shielding, ozone detection + destruct. | Tolerable (with mitigation) | Equipment present in the bill of materials | PASS |  | PASS
Engine advisories (uncorroborated — do not treat as hazards)
# | Category | Advisory (uncorroborated — not a hazard) | Why it does not score / clearing action | Cell check
1 | Engineering — design (physics-critic advisory) | The 'Drive Motor' for the Fertigation Dosing Pump is rated at 7.5 kW, but the parent 'Fertigation Dosing Pump' component is rated at 8 kW. This is a minor mismatch in the drive-train rating reconciliation. | No deterministic check over the delivered artefacts can confirm this claim. · CLEARING ACTION: Stage 7.5 physics-critic LLM output variance, not a design property. The corroboration layer already excludes it from scoring on every run, regardless of how the critic re-phrases the claim on a re-roll — no design action is required and re-running Stage 7.5 is NOT expected to clear it. It will move into the risk register automatically if a future run's deterministic check corroborates it against the delivered design. | PASS
2 | Engineering — design (physics-critic advisory) | The 'Ro High Pressure Pump' has its service block defined as 'rotating_electrical' with fluid 'none' and phase 'none'. Because this pump handles high-pressure water (10.6 bar per the brief), its service block must reflect fluid 'process_water', phase 'liquid', and pressure_bar '10.6'. | No deterministic check over the delivered artefacts can confirm this claim. · CLEARING ACTION: Stage 7.5 physics-critic LLM output variance, not a design property. The corroboration layer already excludes it from scoring on every run, regardless of how the critic re-phrases the claim on a re-roll — no design action is required and re-running Stage 7.5 is NOT expected to clear it. It will move into the risk register automatically if a future run's deterministic check corroborates it against the delivered design. | PASS
3 | Engineering — design (physics-critic advisory) | The 'Drive Motor' for the Ro High Pressure Pump is rated at 4.2 kW, but the parent 'Ro High Pressure Pump' component is rated at 4 kW. This is a minor mismatch in the drive-train rating reconciliation. | No deterministic check over the delivered artefacts can confirm this claim. · CLEARING ACTION: Stage 7.5 physics-critic LLM output variance, not a design property. The corroboration layer already excludes it from scoring on every run, regardless of how the critic re-phrases the claim on a re-roll — no design action is required and re-running Stage 7.5 is NOT expected to clear it. It will move into the risk register automatically if a future run's deterministic check corroborates it against the delivered design. | PASS
4 | Engineering — design (physics-critic advisory) | The 'Differential pH electrode + transmitter' is field-mounted on the 'Drain Water Tank' in this module, but the brief specifies that the pH/EC measuring shunt is located on the fertigation bypass line (Hoogendoorn shunt). | No deterministic check over the delivered artefacts can confirm this claim. · CLEARING ACTION: Stage 7.5 physics-critic LLM output variance, not a design property. The corroboration layer already excludes it from scoring on every run, regardless of how the critic re-phrases the claim on a re-roll — no design action is required and re-running Stage 7.5 is NOT expected to clear it. It will move into the risk register automatically if a future run's deterministic check corroborates it against the delivered design. | PASS
Regulatory & compliance
Jurisdiction: UK · compliance-gate verdict: WARN (0/0 class standards covered). Statutory duties below are derived from the jurisdiction + the hazards present (universal matrix), not a per-class list — verify before sale / construction.
Engine compliance-gate verdict
WARN — No class-standards registered for "water_treatment". Compliance check skipped — engineer must verify manually before sale. | No class-standards registered for "water_treatment". Compliance check skipped — engineer must verify manually before sale.
Statutory duties that always apply (UK)
# | Regulation / standard | Applies because | Status | Cell check
1 | Health and Safety at Work etc. Act 1974 | Overarching duty of care to workers and others. | Mandatory — verify | PASS
2 | Management of Health and Safety at Work Regulations 1999 | Suitable & sufficient risk assessment. | Mandatory — verify | PASS
3 | Construction (Design and Management) Regulations 2015 (CDM) | Design + construction safety duties. | Mandatory — verify | PASS
4 | Supply of Machinery (Safety) Regulations 2008 (UKCA) | Machinery conformity + UKCA marking. | Mandatory — verify | PASS
Hazard-driven regulations (from the equipment present)
# | Regulation / standard | Triggered by (hazard present) | Status | Cell check
1 | Control of Substances Hazardous to Health Regulations 2002 (COSHH) | Toxic / asphyxiant gas release; Chemical handling — corrosive / reactive | Mandatory — verify | PASS
2 | Pressure Systems Safety Regulations 2000 (PSSR) | Stored pressure energy | Mandatory — verify | PASS
3 | Pressure Equipment (Safety) Regulations 2016 | Stored pressure energy | Mandatory — verify | PASS
4 | Provision and Use of Work Equipment Regulations 1998 (PUWER) | Rotating machinery — entanglement / mechanical failure | Mandatory — verify | PASS
5 | Supply of Machinery (Safety) Regulations 2008 (UKCA) | Rotating machinery — entanglement / mechanical failure | Mandatory — verify | PASS
6 | Electricity at Work Regulations 1989 | Electrical — shock / arc-flash | Mandatory — verify | PASS
7 | BS 7671 Requirements for Electrical Installations | Electrical — shock / arc-flash | Mandatory — verify | PASS
8 | Work at Height Regulations 2005 | Working at height / confined space (tanks & vessels) | Mandatory — verify | PASS
9 | Confined Spaces Regulations 1997 | Working at height / confined space (tanks & vessels) | Mandatory — verify | PASS
10 | Environmental Permitting (England and Wales) Regulations 2016 | Environmental discharge to controlled waters | Mandatory — verify | PASS
11 | Dangerous Substances and Explosive Atmospheres Regulations 2002 (DSEAR) | Chemical handling — corrosive / reactive | Mandatory — verify | PASS
12 | Control of Artificial Optical Radiation at Work Regulations 2010 | Radiation — ultraviolet / ozone exposure | Mandatory — verify | PASS

## Holds & exclusions
Holds & exclusions — the honest open-items register | [6 empty] | ↑ Contents
⬤ TAB QUALITY 10/10 · PASS (target ≥8, live from the Quality & Audit score cell) · arithmetic: 10 × min(complete 5/5, impact 5/5, owner 5/5, exclusions cited 5/5); content checks: live-derivation check (each hold re-derived from the current contract re… · full audit: Quality & Audit tab
Every hold is DERIVED LIVE from a failing check or column contract at build time — never hand-typed — so this register is always current: fix the item at source, rebuild, and its hold disappears. Impact is the SAME live count already in Scope, expressed as £ or a scope %; Owner routes to the mechanism that clears it. The dossier ships as a draft WITH these holds against it; the exclusions restate what was never in scope, each reconciled against the client-offer's own named sections.
HOLDS — 5 open item(s), numbered
Hold | Item | Scope (live count) | Impact (£ or %) | Owner | Derived from | Clears when | Cell check
HOLD-001 | Line sizing pending flow allocation | 2 line(s) with no derivable flow (velocity unverifiable) | 2.8 | Process/piping engineering — Line & velocity | Line & velocity column contract (live per-row evaluation) | author the real flow demand on every fluid topology edge at source — the contract then re-passes and this hold clears | PASS
HOLD-002 | Bought-out manufacturer part numbers pending detailed design | 1/61 engineered bought-out lines carry an explicit 'TBD (detailed design)' part number (commodity lines 'MPN at procurement' are tallied separately and carry no hold: 8) | 1.6 | Procurement / detailed design — BoM ledger | Bill of Materials ledger column contract (live TBD count) | resolve real MPNs at detailed design (Stage 17.6 library / supplier RFQs) — the TBD count then falls and this hold clears | PASS
HOLD-003 | Panel circuits failing the schedule column contract | 1/22 circuit row(s) FAIL (missing ΔU / out-of-band volt-drop) | 4.5 | Electrical engineering — Panel schedule | Panel schedule column contract (live per-circuit evaluation) | route + size the failing circuits so ΔU computes in-band | PASS
HOLD-004 | Needs input — coverage_partial | 3 drawing(s) partially covered (worst 83%): panel-schedule: 19/23; pid: 36/39; process-schedules: 20/21 — minor over-decomposition detail; principal systems are represented | 50 | Engine self-repair — Coverage | self-repair loop (severity MED, tab Coverage) | each engineering drawing must represent every PRINCIPAL part; minor decomposition detail may be represented by its parent ¦ repair: no deterministic single-answer fix — human / sou | PASS
HOLD-005 | Needs input — advisory_critic_notes | 4 critic note(s) are UNCORROBORATED by any deterministic check over the delivered artefacts — rendered as advisory, never scored: The 'Drive Motor' for the Fertigation Dosing Pump | 10 | Engine self-repair — Risk & Regulatory | self-repair loop (severity INFO, tab Risk & Regulatory) | a critic finding may score only when corroborated by a deterministic check over delivered artefacts (B3 finding-set extension) ¦ repair: no deterministic single-answer fix — human | PASS
EXCLUSIONS — never in this plant's scope, each reconciled against the client-offer's own sections
• the grow-lighting / assimilation lighting and its switchboards — CONFIRMED outside the reference client offer (no matching section among its 6 named section(s) — a different trade's scope entirely, not merely a £0 line within it)
• the climate / heating, ventilation and cooling hardware and the climate-control computer — cites client-offer section F (Process-control computer)
• the cultivation rack framework — CONFIRMED outside the reference client offer (no matching section among its 6 named section(s) — a different trade's scope entirely, not merely a £0 line within it)
• the building, civil works and excavation — CONFIRMED outside the reference client offer (no matching section among its 6 named section(s) — a different trade's scope entirely, not merely a £0 line within it)
• the main electrical switchboard and the feeder cables to it, and earthing/cable tray/cable penetrations — CONFIRMED outside the reference client offer (no matching section among its 6 named section(s) — a different trade's scope entirely, not merely a £0 line within it)

## Questions for the customer
Questions for the customer — confirm or correct |  |  |  |  | ↑ Contents
⬤ TAB QUALITY 10/10 · PASS (target ≥8, live from the Quality & Audit score cell) · live-derivation check (each question re-derived from the run's own artefacts: brief augmentation, plausibility critic, decisions register, client-offer reconciliation) —… · full audit: Quality & Audit tab
Customers don't know what they want — so every value the engine had to assume, every brief field still missing, every physics contradiction and every unexplained divergence from your offer is a NUMBERED QUESTION here. Each row is derived live from a named engine artefact at build time (never hand-typed): answer it in the brief or record a scope decision, rebuild, and the row disappears. What changes if your answer differs is stated per row.
OPEN QUESTIONS — 5, numbered (each names the artefact that raised it)
Q# | Question for the customer | Why it matters — what changes if the answer differs | Assumption in force (until answered) | Provenance (engine artefact that raised it) | Cell check
Q-001 | What is the required max mass kg? The brief does not state it and no class default exists. | a stated mass cap becomes a hard constraint on the skid/structure and the transport & lifting plan; today nothing bounds the plant's shipped mass | none in force — the field is empty in the design basis; the design proceeds unconstrained on it | brief augmentation (still_missing) — 1-parsed-brief-augmented.json | PASS | SG: How would customer know this?
Q-002 | What is the required operating environment? The brief does not state it and no class default exists. | the ambient min/max drive thermal sizing (heater/chiller duty, derating), material selection and IP ratings; today no ambient-envelope check can run | none in force — the field is empty in the design basis; the design proceeds unconstrained on it | brief augmentation (still_missing) — 1-parsed-brief-augmented.json | PASS
Q-003 | We assumed target process = Continuous chemical process: capture; field-erected fixed plant with closed-loop solvent/reagent recovery and automated… — confirm or correct. | every quantity derived from this field moves if the real value differs (it entered the design as if the brief had stated it) | inferred: Continuous chemical process: capture; field-erected fixed plant with closed-loop solvent/reagent re… — Process inferred from brief mission/description for water_treatment. class-agnostic inference from brief text for unmapped class 'water_tre… | brief augmentation (was_filled) — 1-parsed-brief-augmented.json | PASS
Q-004 | Please review: For each thin sub-module: confirm whether it should be split further OR accept that the sub-module is genuinely a single-component unit. | A thin sub-module may indicate the chain missed components OR that the sub-module truly is simple (e.g. a single moulded enclosure). Without human review you can't tell which. | grammar: 7 sub-module(s) UNDER-DENSE (<5 words; need 5-7 for a real BoM): fertigation_dosing_system::fertigation_dosing_system__primary_assembly (1 words), sensing_instrumentation::sensing_instrument… | design-decisions register — gate-unrepaired::sub_module_word_density (unrepaired_gate, module fertigation_dosing_system) | PASS
Q-005 | Please review: Trim the module overview to only describe what exists in the design data. | Inflated prose creates the false impression of completeness. Same readability concern. | grammar: 2 module(s) name components in overview that are absent from sub-modules (procurement gap): power_distribution: overview mentions 2 concrete components not present in any sub-module word — m… | design-decisions register — gate-unrepaired::module_prose_subset_of_sub_modules (unrepaired_gate, module power_distribution) | PASS

## Quality & Audit
Quality & Audit — every section and tab against the ≥8 floor + the ship gate |  |  |  |  | ↑ Contents
⬤ TAB QUALITY 9/10 · PASS (target ≥8, live from the Quality & Audit score cell) · THE dossier floor — min score of every deterministic section & non-mirror tab (identical to the verdict computation); own content check: floor mirror + audit-surface int… · full audit: Quality & Audit tab
The engine's own quality surface, on one tab: the dossier verdict (stated ONCE, here), every DETERMINISTIC section and every tab scored against the ≥8 floor (the LLM self-audit's opinions render as advisory annotations — visible, never scoring; B3), and the deterministic ship-gate audit findings. The AIM is ≥8 EVERYWHERE — the floor, not the average. See ⚠ Checks for the live arithmetic invariants.
VERDICT: SHIPS · floor 9/10 (min of every DETERMINISTIC section & non-mirror tab — live cells on Quality & Audit; the LLM self-audit is advisory and never floors; ships at ≥8 everywhere)
MIN deterministic section score 9/10 |  | 9/9 deterministic sections ≥8 | LLM self-audit min 5/10 — ADVISORY, uncorroborated; annotates, never floors (B3) · AIM: every section ≥8
Section | Score (deterministic) | vs ≥8 floor | Self-audit opinion (advisory — never floors) | Top defect (why it's below 8) | Cell check
Drawing gates | 10 | PASS ✓ | — |  | PASS
Cost sanity | 10 | PASS ✓ | — |  | PASS
Physics gates | 10 | PASS ✓ | — |  | PASS
Tool archetype | 10 | PASS ✓ | — |  | PASS
Connectivity | 10 | PASS ✓ | — | X-107 Circuit Breakers: missing_input — Electrical component with no upstream power supply. | PASS
Brief compliance | 10 | PASS ✓ | self-audit opinion: 6 — advisory, uncorroborated |  | PASS
Unresolved critic highs | 10 | PASS ✓ | — |  | PASS
Physics fidelity | 10 | PASS ✓ | self-audit opinion: 5 — advisory, uncorroborated | advisory: the LLM critic's own physics opinion is 7/10 — an annotation only, it never scores (B3) | PASS
Performance card | 9 | PASS ✓ | self-audit opinion: 9 — advisory, uncorroborated |  | PASS
Headline (advisory) | — (no deterministic section — the deliverable is scored on the per-tab table below) | ADVISORY — non-gating | self-audit opinion: 9 — advisory, uncorroborated |  | PASS
Bill of materials (advisory) | — (no deterministic section — the deliverable is scored on the per-tab table below) | ADVISORY — non-gating | self-audit opinion: 8 — advisory, uncorroborated |  | PASS
Design narrative (advisory) | — (no deterministic section — the deliverable is scored on the per-tab table below) | ADVISORY — non-gating | self-audit opinion: 8 — advisory, uncorroborated |  | PASS
Engine quality metrics — the dossier's own confidence rating
Deterministic sections at ≥8 (AIM: all) | 9 / 9 |  | AIM: 100%
Min deterministic section score (floors) | 9/10 |  | AIM: 100%
Min self-audit opinion (advisory — never floors) | 5/10 |  | AIM: 100%
Traceability — every number → the brief | 100% |  | AIM: 100%
Calc-coverage — every number shows its formula | 69% |  | AIM: 100%
Per-tab quality — every tab against the ≥8 floor (worst: Executive Summary 9/10; 0 FAIL, 0 UNSCORED). Score = live formula; muted 'Audit:' columns hold the embedded score operands (passed/checked per component + the governing cap).
Tab | Score | vs ≥8 floor | Top issue / coverage gap (fix at source) | Basis — mechanism & caps (stated) | Audit: governing cap | Audit: p1 | Audit: c1 | Audit: p2 | Audit: c2 | Audit: p3 | Audit: c3 | Audit: p4 | Audit: c4 | Audit: p5 | Audit: c5 | Cell check
Executive Summary | 9 | PASS ✓ | capped at the dossier FLOOR (9/10): the cover cannot claim a higher score than its weakest sheet — fix that sheet to raise this one | MIRROR of the dossier floor (min of every deterministic section & non-mirror tab) — re-stamped from the CURRENT scores, never a stale earlier cap; own content check: cover compliance arithmetic (achieved vs target re-evaluated per row) — brief-compli | 10 | [10 empty] | PASS
Quality & Audit | 9 | PASS ✓ |  | THE dossier floor — min score of every deterministic section & non-mirror tab (identical to the verdict computation); own content check: floor mirror + audit-surface integrity (rows tie to the live scorecard) — per-tab table rows name real scored tab | 10 | [10 empty] | PASS
Overview | 10 | PASS ✓ |  | dashboard integrity (every quoted number vs its engine source) — section scores match the engine scorecard 14/14; capex category % = 100 × £ / Σ (per-row arithmetic) 10/10; Σ capex categories ≈ the BoM materials total 1/1; cell completeness+type cont | 10 | 14 | 14 | 10 | 10 | 1 | 1 | 93 | 93 |  |  | PASS
Brief | 10 | PASS ✓ |  | client-offer reconciliation (live section mapping) — client-offer reconciliation sections consistent (incl. decision-covered) 6/6; every live section rendered as a reconciliation row 1/1; cell completeness+type contract 20/20 · score = min over check | 10 | 6 | 6 | 1 | 1 | 20 | 20 |  |  |  |  | PASS
Quantities | 10 | PASS ✓ |  | quantity provenance (source + where-from + used-by per row) — provenance-verified quantity rows 113/113; cell completeness+type contract 339/339 · score = min over checks of 10 × passed/checked | 10 | 113 | 113 | 339 | 339 | [6 empty] | PASS
Calculations | 10 | PASS ✓ |  | worked-calc coverage (every definition resolves to a computed result; inputs populated) + tool-flow consumption — worked-calc definitions resolve to a computed result 13/13; calc input rows carry their value 37/37; tool outputs consumed downstream 37 | 10 | 13 | 13 | 37 | 37 | 37 | 37 | 223 | 223 |  |  | PASS
Bill of Materials (Ledger) | 9.9 | PASS ✓ | 1/61 ENGINEERED bought-out lines carry MPN 'TBD (detailed design)' — an ESTIMATE-stage gap; score = arithmetic − 4 × engineered-TBD-fraction = 10.0 − 0.1 (8 commodity + 2 OEM-proprietary line(s) tallied separately, unpenalised) | column-contract arithmetic: 10 × 417/417 rows passing; content checks: BoM ledger column contract (per-row Row check) — cell completeness+type contract 2895/2917 · score = min over checks of 10 × passed/checked | 9.9 | 2895 | 2917 | [8 empty] | PASS
Cost waterfall | 10 | PASS ✓ |  | cost-waterfall arithmetic ties (each step vs its named costStack anchor; sums close) — waterfall rows tie live to their stated costStack anchor 6/6; assembly/install rows computed live from their factors 7/7; Σ class subtotals ≈ the BoM materials tot | 10 | 6 | 6 | 7 | 7 | 1 | 1 | 67 | 67 |  |  | PASS
Financial model | 10 | PASS ✓ | 1 orphan numeric literal(s) in the financial model (e.g. row 14 col 2) — a model number must be driven, not typed | formula integrity (cells reference drivers; no orphan literals) + scenario arithmetic (live) — model value cells are live formulas or declared (yellow) inputs 225/226; cell completeness+type contract 395/395 · score = min over checks of 10 × passed/c | 10 | 225 | 226 | 395 | 395 | [6 empty] | PASS
Connection trace | 10 | PASS ✓ |  | resolved-endpoint fraction (every ← / → tag must exist) + per-row status — connection rows carry a computed OK status (0 unresolved endpoints, no missing-tie evidence) 49/49; cell completeness+type contract 106/106 · score = min over checks of 10 × p | 10 | 49 | 49 | 106 | 106 | [6 empty] | PASS
Part names | 9.6 | PASS ✓ | parts-ledger: 3 orphan + 1 not-found equipment item(s) — V-107, V-108, V-109, TX-101 | dedupe + completeness (every BoM tag present exactly once) + cross-link + MPN/status coverage (parts-ledger.json) — part tags unique (each physical thing named once) 93/93; every principal carries an MPN or an honest TBD status 93/93; master tags cro | 9.6 | 93 | 93 | 93 | 93 | 65 | 65 | 100 | 104 | 425 | 425 | PASS
Risk & Regulatory | 10 | PASS ✓ |  | column-contract arithmetic: 10 × 8/8 rows passing; content checks: risk-register column contract (per-row triage) — cell completeness+type contract 176/176 · score = min over checks of 10 × passed/checked | 10 | 176 | 176 | [8 empty] | PASS
Assembly sequence | 10 | PASS ✓ | 13/13 steps carry design-derived content (footprint / region groups / schedule quantities / BoM lift mass) | arithmetic: 10 × min(steps 13/13, heavy-lift callouts 1/1, programme reconciliation 1/1); content checks: design-derived step arithmetic — steps with design-derived duration + predecessor 13/13; heavy (>1 t) items called out with a crane class 1/1; c | 10 | 13 | 13 | 1 | 1 | 1 | 1 | 65 | 65 |  |  | PASS
Process schedules | 9.6 | PASS ✓ | cell contract: 16 of 400 required cells empty/invalid across 16 row(s) — e.g. row 26: 'Size' placeholder '—' | schedule column contract (per-cell completeness + type over every schedule row, from the drawings/*.md source) + cross-schedule item-count reconciliation vs the BoM — cross-schedule item-count reconciliation vs the BoM 2/2; cell completeness+type con | 10 | 2 | 2 | 384 | 400 | [6 empty] | PASS
Line & velocity | 9.6 | PASS ✓ | 3/71 rows FAIL the column contract (arithmetic score 10 × 68/71 = 9.6) — e.g. Fresh Water Tank→Nutrient Tank: velocity underivable — no flow demand on the edge and no contract flow/throughput quantity matches either endpoint · Fresh Water Tank→Drain Water Tank: velocity underivable — no flow demand on the edge and no contract flow/throughput quantity matches either endpoint · Motor Control Center→Digital Control Panel: no carried current on the run | column-contract arithmetic: 10 × 68/71 rows passing; content checks: line & velocity column contract (per-row Row check) — cell completeness+type contract 497/497 · score = min over checks of 10 × passed/checked | 10 | 497 | 497 | [8 empty] | PASS
Glossary | 10 | PASS ✓ |  | glossary contract (every term defined + no orphan terms) — every rendered term carries a definition 59/59; terms actually used somewhere in the workbook 59/59 · score = min over checks of 10 × passed/checked | 10 | 59 | 59 | 59 | 59 | [6 empty] | PASS
Electrical | 9.5 | PASS ✓ | 1/22 circuit/board/drawing rows FAIL the column contract (arithmetic score 10 × 21/22 = 9.5) — e.g. single-line ↔ schedule · board hierarchy: board reference(s) absent from the single-line drawing: MAIN DISTRIBUTION BOARD (TP&N) | column-contract arithmetic: 10 × 21/22 rows passing; content checks: panel-schedule column contract + single-line drawing coverage — cell completeness+type contract 179/179 · score = min over checks of 10 × passed/checked | 9.5 | 179 | 179 | [8 empty] | PASS
Design basis | 10 | PASS ✓ | 26/26 basis lines carry a value + a named source; 26/26 carry a unit or are a stated dimensionless ratio; 3/3 live cross-references resolve | arithmetic: 10 × min(sourced 26/26, unit-or-ratio 26/26, cross-ref resolves 3/3); content checks: design-basis completeness arithmetic — basis rows carrying a value + a named source 26/26; numeric values carrying a unit (or a stated dimensionless rat | 10 | 26 | 26 | 26 | 26 | 3 | 3 | 130 | 130 |  |  | PASS
Holds & exclusions | 10 | PASS ✓ | 5 open hold(s) + 5 exclusion(s) — every hold derived live from a failing check/contract, fully quantified (Impact) and routed (Owner); every exclusion explicitly reconciled against the client offer — nothing left as a bare, unlinked disclosure | arithmetic: 10 × min(complete 5/5, impact 5/5, owner 5/5, exclusions cited 5/5); content checks: live-derivation check (each hold re-derived from the current contract results) — holds carrying item/scope/source/clears 5/5; holds carrying a numeric Im | 10 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | PASS
Questions for the customer | 10 | PASS ✓ | 5 open question(s) for the customer — every row derived live from a named engine artefact (brief augmentation / plausibility critic / decisions register / client-offer reconciliation); an answered question disappears on rebuild | live-derivation check (each question re-derived from the run's own artefacts: brief augmentation, plausibility critic, decisions register, client-offer reconciliation) — rendered questions match the LIVE re-derivation (stale/dropped question = fail) | 10 | 5 | 5 | 25 | 25 | [6 empty] | PASS
⚠ Checks | 10 | PASS ✓ | 318/318 invariants pass | fail-count formula: 10 if 0 FAIL else max(0, 8 − 2 × fails) — deterministic invariants pass 129/129; cell completeness+type contract 194/194 · score = min over checks of 10 × passed/checked | 10 | 129 | 129 | 194 | 194 | [6 empty] | PASS
Renders | 10 | PASS ✓ | Render part coverage 27/27 (100%) | render mechanism: parts-ledger coverage × default-size litter × typed-shape × vision-critic verdict (render-vision-critique.json) — drawing part coverage (blender) 27/27 · score = min over checks of 10 × passed/checked | 10 | 27 | 27 | [8 empty] | PASS
GA — General Arrangement | 10 | PASS ✓ | GA part coverage 27/27 (100%) | GA mechanism: parts-ledger coverage × default-size litter × layout-divergence × typed-shape checks — drawing part coverage (general-arrangement) 27/27 · score = min over checks of 10 × passed/checked | 10 | 27 | 27 | [8 empty] | PASS
P&ID | 9 | PASS ✓ | P&ID part coverage 36/39 (92%) | P&ID part-coverage arithmetic (parts_ledger ✓/✗ vs the BoM) — drawing part coverage (pid) 36/39 · score = min over checks of 10 × passed/checked | 9 | 36 | 39 | [8 empty] | PASS
BFD — Block Flow | 10 | PASS ✓ | Block-flow part coverage 18/18 (100%) | block-flow part-coverage arithmetic (parts_ledger) — drawing part coverage (block-flow-diagram) 18/18 · score = min over checks of 10 × passed/checked | 10 | 18 | 18 | [8 empty] | PASS
HVAC | n/a — verified out of scope | VERIFIED — not scored | out of scope for this archetype — VERIFIED, not scored: HVAC's climate hardware (heating / ventilation / cooling) is supplied by others (per the brief), confirmed by both checks below — excluded from the ≥8 floor rather than penalised for having no HVAC engineering to show. | HVAC duty-scoped check: contract duty signal → drawing coverage; no duty → honest out-of-scope disclosure (capped 8) — confirmed no HVAC/ventilation/cooling contract duty (contract quantities scanned) 1/1; brief's own exclusions cite the climate/HVAC | [11 empty] | PASS
Drawings | 9.6 | PASS ✓ | 5 drawing(s) registered with 21 print-ready A1 sheet PDF(s), all present on disk, lettering ≥2.5 mm | drawing-register integrity: every registered A1 print PDF exists on disk + ISO 3098 2.5 mm lettering bar — registered drawings with their print set present 4/4; cell completeness+type contract 27/28 · score = min over checks of 10 × passed/checked | 9.6 | 4 | 4 | 27 | 28 | [6 empty] | PASS
Sense-check | 10 | PASS ✓ |  | generative benchmark sanity net (gate 36): independent top-down LLM expectation diffed against the bottom-up engine, per-dimension — benchmark dimensions within the expectation envelope 4/4; gate-36 verdict is not RADICAL 1/1; cell completeness+type | 10 | 4 | 4 | 1 | 1 | 33 | 33 |  |  |  |  | PASS
Inputs & Assumptions | 9.4 | PASS ✓ | 1 driver(s) never referenced by any live formula (orphan inputs): Design process flow (peak) | driver integrity (every input driver consumed by a live formula) — drivers referenced by a live formula somewhere 17/18; cell completeness+type contract 54/54 · score = min over checks of 10 × passed/checked | 9.4 | 17 | 18 | 54 | 54 | [6 empty] | PASS
Inputs Master (M0) | 10 | PASS ✓ |  | cell completeness+type contract 270/270 · score = min over checks of 10 × passed/checked | 10 | 270 | 270 | [8 empty] | PASS
Equipment & Dimensions Register | 9.9 | PASS ✓ | cell contract: 6 of 423 required cells empty/invalid across 3 row(s) — e.g. row 19: 'Material' placeholder '—'; 'Drawing appearances' placeholder '—' | cell completeness+type contract 417/423 · score = min over checks of 10 × passed/checked | 10 | 417 | 423 | [8 empty] | PASS
Audit data | 10 | PASS ✓ |  | audit-operand register contract (every embedded operand carries its label + provenance; per-row Cell check formulas) — cell completeness+type contract 304/304 · score = min over checks of 10 × passed/checked | 10 | 304 | 304 | [8 empty] | PASS
Contents | 10 | PASS ✓ |  | index integrity (both directions) — index rows point at an existing tab 32/32; every sheet listed in the index 32/32; cell completeness+type contract 96/96 · score = min over checks of 10 × passed/checked | 10 | 32 | 32 | 32 | 32 | 96 | 96 |  |  |  |  | PASS
LIVE FLOOR — min of every deterministic section & non-mirror tab (the ONE VERDICT's number, computed in-cell) | 9
LIVE OPEN ISSUES — sections/tabs below 8 or unscored (computed in-cell over the same score cells) | 0
⚠ Deterministic ship-gate audit — every per-tab check (no LLM)
Findings: 0 HIGH · 1 MED · 0 LOW · 1 total — a HIGH finding means the dossier is NOT validated.
Coverage
Severity | Check | Message | Actual | Expected | Cell check
MED | coverage_partial | 3 drawing(s) partially covered (worst 83%): panel-schedule: 19/23; pid: 36/39; process-schedules: 20/21 — minor over-decomposition detail; principal systems are represented | 3 partial drawings, worst 83% | every principal system represented on each drawing (≥95% coverage) | PASS
Risk & Regulatory
Severity | Check | Message | Actual | Expected | Cell check
INFO | advisory_critic_notes | 4 critic note(s) are UNCORROBORATED by any deterministic check over the delivered artefacts — rendered as advisory, never scored: The 'Drive Motor' for the Fertigation Dosing Pump is rated at 7.5… ¦ The 'Ro High Pressure Pump' has its service block defined as… | 4 advisory notes | advisory notes are visible but carry no score penalty | PASS
BENCHMARK NET — independent generative-LLM expectation (top-down) vs the engine (bottom-up)
deterministic output deviates from the benchmark — review recommended · model: z-ai/glm-5.2 · worst verdict: warn
Dimension | LLM expected (top-down) | Engine (bottom-up) | Ratio | Verdict / note | Cell check
all-in cost | £800,000–1,400,000 (mid £1,100,000) | £1,120,505 (costStack.oem_transfer_price_gbp) | 1.02× |  | ⚠ FAIL — a required cell is empty/placeholder or wrong type
output — irrigation_flow | 45 m3/h | 90 m3/h (contract.irrigation_pump_flow_m3_h) | 2.00× |  | ⚠ FAIL — a required cell is empty/placeholder or wrong type
output — ro_permeate_flow | 8 m3/h | 8 m³/h (contract.ro_permeate_capacity_m3_h) | 1.00× |  | ⚠ FAIL — a required cell is empty/placeholder or wrong type
output — storage_capacity | 120 m3 | 120 m3 (contract.water_storage_delivered_m3) | 1.00× |  | ⚠ FAIL — a required cell is empty/placeholder or wrong type

## Sense-check
Independent sense-check — generative LLM expectation vs the deterministic engine
⬤ TAB QUALITY 10/10 · PASS (target ≥8, live from the Quality & Audit score cell) · generative benchmark sanity net (gate 36): independent top-down LLM expectation diffed against the bottom-up engine, per-dimension — benchmark dimensions within the expe… · full audit: Quality & Audit tab
An LLM independently estimates, TOP-DOWN from the market, what a plant like this should cost, output and be built from. The deterministic engine builds BOTTOM-UP from parts. The two methods are diffed: a large gap means one is wrong. This is the engine's own sanity check — shown here so you can see it, not just trust it.
SENSE-CHECK VERDICT: WARN |  |  |  | deterministic output deviates from the benchmark — review recommended
All-in cost — LLM top-down envelope vs the engine
| LLM expected (top-down) | Engine (bottom-up) | Ratio | Basis | Cell check
All-in cost | £800,000–£1,400,000 (mid £1,100,000) | £1,120,505 | 1.0× | Highly automated 45 m3/h irrigation distribution with 200 actuated valves and 8 m3/h RO skid typically runs £18k-30k per m3/h of total flow due to heavy automation and piping scope. | PASS
Per-dimension divergence — 4 checked (cost · output · sizing · components)
Dimension | LLM expected | Engine (deterministic) | Ratio | Verdict | Cell check
all-in cost | £800,000–1,400,000 (mid £1,100,000) | £1,120,505 (costStack.oem_transfer_price_gbp) | 1.0× | ok | PASS
output — irrigation_flow | 45 m3/h | 90 m3/h (contract.irrigation_pump_flow_m3_h) | 2.0× | warn | PASS
output — ro_permeate_flow | 8 m3/h | 8 m³/h (contract.ro_permeate_capacity_m3_h) | 1.0× | ok | PASS
output — storage_capacity | 120 m3 | 120 m3 (contract.water_storage_delivered_m3) | 1.0× | ok | PASS
Per-line-item faults — 7 lines the LLM flags as wrong in the engine's bill
Bill line | What's wrong | Magnitude | LLM-suggested | Likely cause | Cell check
P-103 | Irrigation pump specified at 90 m³/h instead of required 45 m³/h | 2× too high | 45 m³/h pump | wrong sizing parameter propagated from contract.irrigation_pump_flow_m3_h | PASS
— ¦ qty 8280 ¦ unit £13.2 ¦ Zoned distribution — zone laterals (flood-fill lines) · DN75 PVC | Qty 8280 (likely metres or segments) far exceeds small-warehouse scale | ~10-20× too high | ~400-800 m total | wrong quantity / treated reel-or-sheet price as per-unit | PASS
— ¦ qty 4200 ¦ unit £20.8 ¦ Zoned distribution — drain/return risers (gravity) · DN110 PVC-U | Qty 4200 excessive for plant footprint | ~10× too high | ~400 m | wrong quantity | PASS
— ¦ qty 6000 ¦ unit £6 ¦ Zoned distribution — delivery inlet stubs | Qty 6000 stubs impossible for small plant | ~30× too high | ~200 stubs | wrong quantity / per-cell commodity error | PASS
— ¦ qty 3000 ¦ unit £9 ¦ Zoned distribution — drain outlet connections | Qty 3000 excessive | ~15× too high | ~200 connections | wrong quantity | PASS
TK-106 ¦ qty 2 ¦ unit £13615 ¦ Drain Water Tank · 3.7 m dia x 3.7 m | Individual tanks ~40 m³; total storage meets 120 m³ only if all tanks combined, but labelled as drain not general storage | mis-classified / undersized per tank | one 120 m³ or 3×40 m³ fresh-water tanks | wrong size-or-volume / mis-classified commodity | PASS
FCV-201–202 | Inlet control valve rated 45 m³/h while irrigation pump is 90 m³/h | inconsistent with pump | 90 m³/h valve or align pump to 45 | inconsistent flow parameter | PASS
LLM-expected bill structure (top-down — what the cost SHOULD break into)
Expected line / category | % of cost | Note |  |  | Cell check
Piping, Fittings & Actuated Valves | 35% | 200 actuated valves plus extensive distribution to 6000 containers dominates |  |  | PASS
Automation, Control & Instrumentation | 20% | PLC/SCADA to manage 200 valves and process logic |  |  | PASS
Pumps & Storage | 15% | 120 m3 tank and distribution/booster pumps |  |  | PASS
Treatment Skids (RO, Filtration, UV) | 15% | 8 m3/h RO and pre/post treatment |  |  | PASS
Civil, Structural & Installation Labor | 15% | Trenching, skid mounting, container integration |  |  | PASS
LLM reasoning (how the top-down expectation was formed)
While the raw water treatment capacity (45 m3/h) is modest, the sheer scale of automation (200 actuated valves) and distribution (6000 cultivation containers) drives the cost toward the £1M+ mark, making the £1.4M ceiling realistic but tight. The bill of materials is dominated by mechanical piping/valves and the control system required to orchestrate the complex irrigation network, rather than the water treatment technology itself.

## ⚠ Checks
⚠ Computational checks — live invariants (== the CLI verifier) | [6 empty] | ↑ Contents
⬤ TAB QUALITY 10/10 · PASS (target ≥8, live from the Quality & Audit score cell) · fail-count formula: 10 if 0 FAIL else max(0, 8 − 2 × fails) — deterministic invariants pass 129/129; cell completeness+type contract 194/194 · score = min over checks of… · full audit: Quality & Audit tab
EXACTLY the checks scripts/deterministic-checks.py reports, rendered as LIVE Excel formulas over the data cells (cols J+). Edit a data cell and STATUS recomputes. RED = the engine's numbers do not reconcile.
Check | ACTUAL | EXPECTED | Δ (actual-exp) | Tol | STATUS | Detail / why | Cell check |  | DATA (live inputs — editable) |  |  |  |  | AGGREGATE DATA — one row per collapsed per-line invariant (P=line · Q=per-unit/actual £ · R=expected £ · S=qty · T=live mismatch flag). Edit Q/R/S and the aggregate row recomputes.
E1 · CONSISTENCY — per-unit×count, Σsub==line, rating==quantity | [13 empty] | BoM X-104: unit_gbp x qty == line_gbp | 800 | 800 | 1 | 0
All 173 BoM lines: unit £ × qty == line £ (aggregate — mismatching lines list individually) | 0 | 0 | 0 | 0 | PASS | 173 per-line invariants collapsed — each line lives in the DATA block (cols P–T, rows 5–177) with a LIVE mismatch flag at its own tolerance; ACTUAL = the number of mismatching lines. 0 exception(s) below. | PASS |  | All 173 BoM lines: unit £ × qty == line £ (aggregate — mismatching lines list individually) |  | 0 |  |  | BoM X-107: unit_gbp x qty == line_gbp | 283 | 283 | 1 | 0
All 17 BoM lines: Σ sub-component £ == line £ (aggregate — mismatching lines list individually) | 0 | 0 | 0 | 0 | PASS | 17 per-line invariants collapsed — each line lives in the DATA block (cols P–T, rows 178–194) with a LIVE mismatch flag at its own tolerance; ACTUAL = the number of mismatching lines. 0 exception(s) below. | PASS |  | All 17 BoM lines: Σ sub-component £ == line £ (aggregate — mismatching lines list individually) |  | 0 |  |  | BoM X-108: unit_gbp x qty == line_gbp | 1 | 1 | 1 | 0
BoM V-102: emitted kW rating == uv_disinfection_power_kw | 4 | 4.1 | -0.1 | 0.5 | PASS | V-102 requirement states 4 kW; contract uv_disinfection_power_kw = 4.1 kW. They must agree. | PASS |  | BoM V-102: emitted kW rating == uv_disinfection_power_kw | 4 | 4.1 |  |  | BoM D-101: unit_gbp x qty == line_gbp | 168 | 168 | 1 | 0
BoM P-106: emitted kW rating == fertigation_dosing_pump_power_kw | 8 | 7.5 | 0.5 | 0.75 | PASS | P-106 requirement states 8 kW; contract fertigation_dosing_pump_power_kw = 7.5 kW. They must agree. | PASS |  | BoM P-106: emitted kW rating == fertigation_dosing_pump_power_kw | 8 | 7.5 |  |  | BoM X-109: unit_gbp x qty == line_gbp | 3 | 3 | 1 | 0
BoM P-104: emitted kW rating == drain_transfer_pump_power_kw | 2 | 1.923 | 0.077 | 0.5 | PASS | P-104 requirement states 2 kW; contract drain_transfer_pump_power_kw = 1.923 kW. They must agree. | PASS |  | BoM P-104: emitted kW rating == drain_transfer_pump_power_kw | 2 | 1.923 |  |  | BoM G-201: unit_gbp x qty == line_gbp | 19200 | 19200 | 1 | 0
BoM P-101: emitted kW rating == ro_high_pressure_pump_power_kw | 4 | 4.2 | -0.2 | 0.5 | PASS | P-101 requirement states 4 kW; contract ro_high_pressure_pump_power_kw = 4.2 kW. They must agree. | PASS |  | BoM P-101: emitted kW rating == ro_high_pressure_pump_power_kw | 4 | 4.2 |  |  | BoM U-201: unit_gbp x qty == line_gbp | 4000 | 4000 | 1 | 0
modules: every described sub-module carries components (no hollow module) | 0 | 0 | 0 | 0 | PASS | every sub-module that describes components backs its prose with ≥1 component word | PASS |  | modules: every described sub-module carries components (no hollow module) | 0 | 0 |  |  | BoM EP-103: unit_gbp x qty == line_gbp | 62650 | 62650 | 1 | 0
[14 empty] | BoM TX-102: unit_gbp x qty == line_gbp | 3000 | 3000 | 1 | 0
E2 · ADEQUACY — rating ≥ duty (motor, breaker, cable, vessel, chiller) | [13 empty] | BoM EP-104: unit_gbp x qty == line_gbp | 3000 | 3000 | 1 | 0
Main incomer kVA >= connected load x 1.25 | 75 | 66.25 | 8.75 | 0 | PASS | Incomer 75 kVA (total_supply_demand_kva) must be >= 53 kW x 1.25 = 66.25 kVA (kVA >= kW for any power factor); magnitude sanity ceiling <= connected load 53 kW x 100 = 5300 (an absurdly-large rating must FAIL, not pass as 'adequate'). |  |  | Main incomer kVA >= connected load x 1.25 | 75 | 66.25 |  |  | BoM X-110: unit_gbp x qty == line_gbp | 283 | 283 | 1 | 0
Cable CSA >= ampacity: Standby Diesel Generator | 1.5 | 1.5 | 0 | 0 | PASS | Mains Incomer->Standby Diesel Generator: 4.2 A needs >= 1.5 mm2 copper (air-rated ladder); chosen 1.5 mm2. |  |  | Cable CSA >= ampacity: Standby Diesel Generator | 1.5 | 1.5 |  |  | BoM X-111: unit_gbp x qty == line_gbp | 2 | 2 | 1 | 0
Cable CSA >= ampacity: Distribution Transformer | 1.5 | 1.5 | 0 | 0 | PASS | Standby Diesel Gen->Distribution Transformer: 4.2 A needs >= 1.5 mm2 copper (air-rated ladder); chosen 1.5 mm2. |  |  | Cable CSA >= ampacity: Distribution Transformer | 1.5 | 1.5 |  |  | BoM F-1: unit_gbp x qty == line_gbp | 9100 | 9100 | 1 | 0
Cable CSA >= ampacity: Main Switchboard | 1.5 | 1.5 | 0 | 0 | PASS | Distribution Trans->Main Switchboard: 4.2 A needs >= 1.5 mm2 copper (air-rated ladder); chosen 1.5 mm2. |  |  | Cable CSA >= ampacity: Main Switchboard | 1.5 | 1.5 |  |  | BoM X-112: unit_gbp x qty == line_gbp | 1 | 1 | 1 | 0
Cable CSA >= ampacity: Motor Control Center | 1.5 | 1.5 | 0 | 0 | PASS | Main Switchboard->Motor Control Center: 4.2 A needs >= 1.5 mm2 copper (air-rated ladder); chosen 1.5 mm2. |  |  | Cable CSA >= ampacity: Motor Control Center | 1.5 | 1.5 |  |  | BoM V-102: unit_gbp x qty == line_gbp | 17540 | 17540 | 1 | 0
Cable CSA >= ampacity: Electrical Control Panel | 1.5 | 1.5 | 0 | 0 | PASS | Motor Control Cent->Electrical Control Panel: 4.2 A needs >= 1.5 mm2 copper (air-rated ladder); chosen 1.5 mm2. |  |  | Cable CSA >= ampacity: Electrical Control Panel | 1.5 | 1.5 |  |  | BoM V-106: unit_gbp x qty == line_gbp | 8000 | 16000 | 2 | 0
Cable CSA >= ampacity: 3 Phase Power Input | 1.5 | 1.5 | 0 | 0 | PASS | Motor Control Cent->3 Phase Power Input: 4.2 A needs >= 1.5 mm2 copper (air-rated ladder); chosen 1.5 mm2. |  |  | Cable CSA >= ampacity: 3 Phase Power Input | 1.5 | 1.5 |  |  | BoM P-106: unit_gbp x qty == line_gbp | 8634 | 17268 | 2 | 0
Cable CSA >= ampacity: Control + Instrument UPS | 1.5 | 1.5 | 0 | 0 | PASS | Motor Control Cent->Control + Instrument UPS: 4.2 A needs >= 1.5 mm2 copper (air-rated ladder); chosen 1.5 mm2. |  |  | Cable CSA >= ampacity: Control + Instrument UPS | 1.5 | 1.5 |  |  | BoM TK-103: unit_gbp x qty == line_gbp | 2844 | 22752 | 8 | 0
Cable CSA >= ampacity: SCADA / Plant Control Sy | 1.5 | 1.5 | 0 | 0 | PASS | Motor Control Cent->SCADA / Plant Control Sy: 4.2 A needs >= 1.5 mm2 copper (air-rated ladder); chosen 1.5 mm2. |  |  | Cable CSA >= ampacity: SCADA / Plant Control Sy | 1.5 | 1.5 |  |  | BoM P-102: unit_gbp x qty == line_gbp | 2500 | 2500 | 1 | 0
Cable CSA >= ampacity: Uv Disinfection | 1.5 | 1.5 | 0 | 0 | PASS | Motor Control Cent->Uv Disinfection: 8.2 A needs >= 1.5 mm2 copper (air-rated ladder); chosen 1.5 mm2. |  |  | Cable CSA >= ampacity: Uv Disinfection | 1.5 | 1.5 |  |  | BoM TK-114: unit_gbp x qty == line_gbp | 4683 | 9366 | 2 | 0
Cable CSA >= ampacity: Fertigation Dosing Pump | 1.5 | 1.5 | 0 | 0 | PASS | Motor Control Cent->Fertigation Dosing Pump: 15 A needs >= 1.5 mm2 copper (air-rated ladder); chosen 1.5 mm2. |  |  | Cable CSA >= ampacity: Fertigation Dosing Pump | 1.5 | 1.5 |  |  | BoM P-104: unit_gbp x qty == line_gbp | 1850 | 3700 | 2 | 0
Cable CSA >= ampacity: Hand Watering Pump | 1.5 | 1.5 | 0 | 0 | PASS | Motor Control Cent->Hand Watering Pump: 4.2 A needs >= 1.5 mm2 copper (air-rated ladder); chosen 1.5 mm2. |  |  | Cable CSA >= ampacity: Hand Watering Pump | 1.5 | 1.5 |  |  | BoM V-104: unit_gbp x qty == line_gbp | 8270 | 16540 | 2 | 0
Cable CSA >= ampacity: Drain Transfer Pump | 1.5 | 1.5 | 0 | 0 | PASS | Motor Control Cent->Drain Transfer Pump: 3.9 A needs >= 1.5 mm2 copper (air-rated ladder); chosen 1.5 mm2. |  |  | Cable CSA >= ampacity: Drain Transfer Pump | 1.5 | 1.5 |  |  | BoM V-103: unit_gbp x qty == line_gbp | 14825 | 14825 | 1 | 0
Cable CSA >= ampacity: Cloth Filter | 1.5 | 1.5 | 0 | 0 | PASS | Motor Control Cent->Cloth Filter: 4.2 A needs >= 1.5 mm2 copper (air-rated ladder); chosen 1.5 mm2. |  |  | Cable CSA >= ampacity: Cloth Filter | 1.5 | 1.5 |  |  | BoM P-103: unit_gbp x qty == line_gbp | 9413 | 9413 | 1 | 0
Cable CSA >= ampacity: Irrigation Pump | 1.5 | 1.5 | 0 | 0 | PASS | Motor Control Cent->Irrigation Pump: 4.2 A needs >= 1.5 mm2 copper (air-rated ladder); chosen 1.5 mm2. |  |  | Cable CSA >= ampacity: Irrigation Pump | 1.5 | 1.5 |  |  | BoM M-101: unit_gbp x qty == line_gbp | 1725 | 3450 | 2 | 0
Cable CSA >= ampacity: Ro High Pressure Pump | 1.5 | 1.5 | 0 | 0 | PASS | Motor Control Cent->Ro High Pressure Pump: 8.4 A needs >= 1.5 mm2 copper (air-rated ladder); chosen 1.5 mm2. |  |  | Cable CSA >= ampacity: Ro High Pressure Pump | 1.5 | 1.5 |  |  | BoM Z-101: unit_gbp x qty == line_gbp | 8737 | 8737 | 1 | 0
Cable CSA >= ampacity: Gac Filter | 1.5 | 1.5 | 0 | 0 | PASS | Motor Control Cent->Gac Filter: 4.2 A needs >= 1.5 mm2 copper (air-rated ladder); chosen 1.5 mm2. |  |  | Cable CSA >= ampacity: Gac Filter | 1.5 | 1.5 |  |  | BoM P-101: unit_gbp x qty == line_gbp | 3850 | 3850 | 1 | 0
Cable CSA >= ampacity: Permeate Outlet | 1.5 | 1.5 | 0 | 0 | PASS | Motor Control Cent->Permeate Outlet: 4.2 A needs >= 1.5 mm2 copper (air-rated ladder); chosen 1.5 mm2. |  |  | Cable CSA >= ampacity: Permeate Outlet | 1.5 | 1.5 |  |  | BoM V-101: unit_gbp x qty == line_gbp | 18 | 18 | 1 | 0
Cable CSA >= ampacity: Concentrate Outlet | 1.5 | 1.5 | 0 | 0 | PASS | Motor Control Cent->Concentrate Outlet: 4.2 A needs >= 1.5 mm2 copper (air-rated ladder); chosen 1.5 mm2. |  |  | Cable CSA >= ampacity: Concentrate Outlet | 1.5 | 1.5 |  |  | BoM TK-108: unit_gbp x qty == line_gbp | 13615 | 13615 | 1 | 0
Cable CSA >= ampacity: Electrical Control Cabin | 1.5 | 1.5 | 0 | 0 | PASS | Motor Control Cent->Electrical Control Cabin: 4.2 A needs >= 1.5 mm2 copper (air-rated ladder); chosen 1.5 mm2. |  |  | Cable CSA >= ampacity: Electrical Control Cabin | 1.5 | 1.5 |  |  | BoM TK-106: unit_gbp x qty == line_gbp | 13615 | 27230 | 2 | 0
[14 empty] | BoM X-113: unit_gbp x qty == line_gbp | 3 | 3 | 1 | 0
E4 · COST — per-line price band & Σ lines == cover total | [13 empty] | BoM F-2: unit_gbp x qty == line_gbp | 9100 | 9100 | 1 | 0
BoM X-104: unit price within x5 of price_estimate_gbp | 800 | 285.53 | 514.47 | 5 | PASS | X-104 (Rittal 1180.000): BoM unit £800 vs price_estimate_gbp £286 = x2.8. Flag when >x5 or <x0.2. |  |  | BoM X-104: unit price within x5 of price_estimate_gbp | 800 | 285.53 |  | 0 | BoM X-114: unit_gbp x qty == line_gbp | 160 | 160 | 1 | 0
BoM X-107: unit price within x5 of distributor_price_gbp | 283 | 283 | 0 | 5 | PASS | X-107 (ABB 1SDA067417R1): BoM unit £283 vs distributor_price_gbp £283 = x1.0. Flag when >x5 or <x0.2. |  |  | BoM X-107: unit price within x5 of distributor_price_gbp | 283 | 283 |  | 0 | BoM X-115: unit_gbp x qty == line_gbp | 12 | 12 | 1 | 0
BoM X-108: unit price within x5 of distributor_price_gbp | 1 | 1.2 | -0.2 | 5 | PASS | X-108 (WAGO 2002-1301): BoM unit £1 vs distributor_price_gbp £1 = x0.8. Flag when >x5 or <x0.2. |  |  | BoM X-108: unit price within x5 of distributor_price_gbp | 1 | 1.2 |  | 0 | BoM X-116: unit_gbp x qty == line_gbp | 160 | 160 | 1 | 0
BoM D-101: unit price within x5 of distributor_price_gbp | 168 | 168 | 0 | 5 | PASS | D-101 (TDK-Lambda DRB240-24-3-A0): BoM unit £168 vs distributor_price_gbp £168 = x1.0. Flag when >x5 or <x0.2. |  |  | BoM D-101: unit price within x5 of distributor_price_gbp | 168 | 168 |  | 0 | BoM X-117: unit_gbp x qty == line_gbp | 330 | 330 | 1 | 0
BoM TX-102: unit price within x5 of price_estimate_gbp | 3000 | 3000 | 0 | 5 | PASS | TX-102 (Hammond Power Solutions SG3A0075KB): price GROUNDED to the market band (£3,000); the pre-grounding price_estimate_gbp £18 was rejected as out-of-band — banding against it is not meaningful. |  |  | BoM TX-102: unit price within x5 of price_estimate_gbp | 3000 | 3000 |  | 0 | BoM X-118: unit_gbp x qty == line_gbp | 982 | 982 | 1 | 0
BoM EP-104: unit price within x5 of price_estimate_gbp | 3000 | 3000 | 0 | 5 | PASS | EP-104 (Eaton Freedom 2100): price DELIBERATELY CORRECTED by the pricing pass (£3,000; basis: catalogue · floored to min credible price); the parametric price_estimate_gbp £25 was rejected/superseded by that correction — banding against it is self-contradictory. |  |  | BoM EP-104: unit price within x5 of price_estimate_gbp | 3000 | 3000 |  | 0 | BoM X-119: unit_gbp x qty == line_gbp | 12 | 12 | 1 | 0
BoM X-110: unit price within x5 of distributor_price_gbp | 283 | 283 | 0 | 5 | PASS | X-110 (ABB 1SDA067417R1): BoM unit £283 vs distributor_price_gbp £283 = x1.0. Flag when >x5 or <x0.2. |  |  | BoM X-110: unit price within x5 of distributor_price_gbp | 283 | 283 |  | 0 | BoM X-120: unit_gbp x qty == line_gbp | 589 | 589 | 1 | 0
BoM V-102: unit price within x5 of price_estimate_gbp | 17540 | 12012 | 5528 | 5 | PASS | V-102 (WEDECO (Xylem) Spektron 30e): BoM unit £17,540 vs price_estimate_gbp £12,012 = x1.5. Flag when >x5 or <x0.2. |  |  | BoM V-102: unit price within x5 of price_estimate_gbp | 17540 | 12012 |  | 0 | BoM X-121: unit_gbp x qty == line_gbp | 160 | 160 | 1 | 0
BoM P-106: unit price within x5 of price_estimate_gbp | 8634 | 8634 | 0 | 5 | PASS | P-106 (Grundfos 96122012): BoM unit £8,634 vs price_estimate_gbp £8,634 = x1.0. Flag when >x5 or <x0.2. |  |  | BoM P-106: unit price within x5 of price_estimate_gbp | 8634 | 8634 |  | 0 | BoM X-122: unit_gbp x qty == line_gbp | 380 | 380 | 1 | 0
BoM P-102: unit price within x5 of price_estimate_gbp | 2500 | 2500 | 0 | 5 | PASS | P-102 (Grundfos 96935501): price GROUNDED to the market band (£2,500); the pre-grounding price_estimate_gbp £8,110 was rejected as out-of-band — banding against it is not meaningful. |  |  | BoM P-102: unit price within x5 of price_estimate_gbp | 2500 | 2500 |  | 0 | BoM X-123: unit_gbp x qty == line_gbp | 280 | 280 | 1 | 0
BoM P-104: unit price within x5 of price_estimate_gbp | 1850 | 7319.38 | -5469.38 | 5 | PASS | P-104 (Grundfos SL1.50.65.22.2.50D.C): BoM unit £1,850 vs price_estimate_gbp £7,319 = x0.3. Flag when >x5 or <x0.2. |  |  | BoM P-104: unit price within x5 of price_estimate_gbp | 1850 | 7319.38 |  | 0 | BoM I-103: unit_gbp x qty == line_gbp | 850 | 850 | 1 | 0
BoM V-103: unit price within x5 of price_estimate_gbp | 14825 | 14825 | 0 | 5 | PASS | V-103 (Pentair Structural 36X72 COMP 6"TF 6"BF): BoM unit £14,825 vs price_estimate_gbp £14,825 = x1.0. Flag when >x5 or <x0.2. |  |  | BoM V-103: unit price within x5 of price_estimate_gbp | 14825 | 14825 |  | 0 | BoM X-124: unit_gbp x qty == line_gbp | 393 | 393 | 1 | 0
BoM P-103: unit price within x5 of price_estimate_gbp | 9413 | 9413 | 0 | 5 | PASS | P-103 (Grundfos 96539165): BoM unit £9,413 vs price_estimate_gbp £9,413 = x1.0. Flag when >x5 or <x0.2. |  |  | BoM P-103: unit price within x5 of price_estimate_gbp | 9413 | 9413 |  | 0 | BoM X-125: unit_gbp x qty == line_gbp | 200 | 40000 | 200 | 0
BoM P-101: unit price within x5 of price_estimate_gbp | 3850 | 8470 | -4620 | 5 | PASS | P-101 (Grundfos 96502039): BoM unit £3,850 vs price_estimate_gbp £8,470 = x0.5. Flag when >x5 or <x0.2. |  |  | BoM P-101: unit price within x5 of price_estimate_gbp | 3850 | 8470 |  | 0 | BoM X-126: unit_gbp x qty == line_gbp | 18 | 18 | 1 | 0
BoM V-101: unit price within x5 of price_estimate_gbp | 18 | 4.5 | 13.5 | 5 | PASS | V-101 (General Carbon HP-1000): BoM unit £18 vs price_estimate_gbp £4 = x4.0. Flag when >x5 or <x0.2. |  |  | BoM V-101: unit price within x5 of price_estimate_gbp | 18 | 4.5 |  | 0 | BoM FCV-201–202: unit_gbp x qty == line_gbp | 3312 | 6624 | 2 | 0
BoM X-114: unit price within x5 of distributor_price_gbp | 160 | 160 | 0 | 5 | PASS | X-114 (Siemens 6ES7241-1CH32-0XB0): BoM unit £160 vs distributor_price_gbp £160 = x1.0. Flag when >x5 or <x0.2. |  |  | BoM X-114: unit price within x5 of distributor_price_gbp | 160 | 160 |  | 0 | BoM V-107: unit_gbp x qty == line_gbp | 393 | 393 | 1 | 0
BoM X-116: unit price within x5 of distributor_price_gbp | 160 | 160 | 0 | 5 | PASS | X-116 (Siemens 6ES7241-1CH32-0XB0): BoM unit £160 vs distributor_price_gbp £160 = x1.0. Flag when >x5 or <x0.2. |  |  | BoM X-116: unit price within x5 of distributor_price_gbp | 160 | 160 |  | 0 | BoM V-108: unit_gbp x qty == line_gbp | 200 | 200 | 1 | 0
BoM X-117: unit price within x5 of price_estimate_gbp | 330 | 330 | 0 | 5 | PASS | X-117 (HMS Networks AB7072-B): BoM unit £330 vs price_estimate_gbp £330 = x1.0. Flag when >x5 or <x0.2. |  |  | BoM X-117: unit price within x5 of price_estimate_gbp | 330 | 330 |  | 0 | BoM I-104: unit_gbp x qty == line_gbp | 12 | 12 | 1 | 0
BoM X-118: unit price within x5 of price_estimate_gbp | 982 | 280 | 702 | 5 | PASS | X-118 (HMS Networks (Ewon) FLEXY20500_00MA): BoM unit £982 vs price_estimate_gbp £280 = x3.5. Flag when >x5 or <x0.2. |  |  | BoM X-118: unit price within x5 of price_estimate_gbp | 982 | 280 |  | 0 | BoM I-105: unit_gbp x qty == line_gbp | 691 | 691 | 1 | 0
BoM X-120: unit price within x5 of distributor_price_gbp | 589 | 589 | 0 | 5 | PASS | X-120 (Panasonic Industrial Automation AWHS1R070): BoM unit £589 vs distributor_price_gbp £589 = x1.0. Flag when >x5 or <x0.2. |  |  | BoM X-120: unit price within x5 of distributor_price_gbp | 589 | 589 |  | 0 | BoM I-106: unit_gbp x qty == line_gbp | 12 | 12 | 1 | 0
BoM X-121: unit price within x5 of distributor_price_gbp | 160 | 160 | 0 | 5 | PASS | X-121 (Siemens 6ES7241-1CH32-0XB0): BoM unit £160 vs distributor_price_gbp £160 = x1.0. Flag when >x5 or <x0.2. |  |  | BoM X-121: unit price within x5 of distributor_price_gbp | 160 | 160 |  | 0 | BoM I-107: unit_gbp x qty == line_gbp | 12 | 12 | 1 | 0
BoM X-122: unit price within x5 of price_estimate_gbp | 380 | 380 | 0 | 5 | PASS | X-122 (Moxa MGate MB3180): BoM unit £380 vs price_estimate_gbp £380 = x1.0. Flag when >x5 or <x0.2. |  |  | BoM X-122: unit price within x5 of price_estimate_gbp | 380 | 380 |  | 0 | BoM LT-201–213: unit_gbp x qty == line_gbp | 1843 | 23959 | 13 | 0
BoM X-123: unit price within x5 of price_estimate_gbp | 280 | 280 | 0 | 5 | PASS | X-123 (HMS Networks (Ewon) FLEXY20500_00MA): BoM unit £280 vs price_estimate_gbp £280 = x1.0. Flag when >x5 or <x0.2. |  |  | BoM X-123: unit price within x5 of price_estimate_gbp | 280 | 280 |  | 0 | BoM LT-214: unit_gbp x qty == line_gbp | 1843 | 1843 | 1 | 0
BoM I-103: unit price within x5 of distributor_price_gbp | 850 | 850 | 0 | 5 | PASS | I-103 (Siemens 6AV2123-2GB03-0AX0): BoM unit £850 vs distributor_price_gbp £850 = x1.0. Flag when >x5 or <x0.2. |  |  | BoM I-103: unit price within x5 of distributor_price_gbp | 850 | 850 |  | 0 | BoM LT-215–217: unit_gbp x qty == line_gbp | 1843 | 5529 | 3 | 0
BoM X-124: unit price within x5 of distributor_price_gbp | 393 | 393.05 | -0.05 | 5 | PASS | X-124 (Sensata Technologies, Inc. SOL7A4): BoM unit £393 vs distributor_price_gbp £393 = x1.0. Flag when >x5 or <x0.2. |  |  | BoM X-124: unit price within x5 of distributor_price_gbp | 393 | 393.05 |  | 0 | BoM AT-201: unit_gbp x qty == line_gbp | 2800 | 2800 | 1 | 0
BoM X-125: unit price within x5 of price_estimate_gbp | 200 | 200 | 0 | 5 | PASS | X-125 (Bürkert Type 2000): price DELIBERATELY CORRECTED by the pricing pass (£200; basis: actuated-valve assembly (actuator + valve body as ONE unit): £80 base + £1.85/DN); the parametric price_estimate_gbp £35 was rejected/superseded by that correction — banding against it is self-contradictory. |  |  | BoM X-125: unit price within x5 of price_estimate_gbp | 200 | 200 |  | 0 | BoM PT-201–217: unit_gbp x qty == line_gbp | 700 | 11900 | 17 | 0
BoM X-126: unit price within x5 of price_estimate_gbp | 18 | 18 | 0 | 5 | PASS | X-126 (Pentair Fleck 2900S): BoM unit £18 vs price_estimate_gbp £18 = x1.0. Flag when >x5 or <x0.2. |  |  | BoM X-126: unit price within x5 of price_estimate_gbp | 18 | 18 |  | 0 | BoM I-108: unit_gbp x qty == line_gbp | 280 | 280 | 1 | 0
BoM V-107: unit price within x5 of distributor_price_gbp | 393 | 393.05 | -0.05 | 5 | PASS | V-107 (Sensata Technologies, Inc. SOL7A4): BoM unit £393 vs distributor_price_gbp £393 = x1.0. Flag when >x5 or <x0.2. |  |  | BoM V-107: unit price within x5 of distributor_price_gbp | 393 | 393.05 |  | 0 | BoM I-109: unit_gbp x qty == line_gbp | 12 | 12 | 1 | 0
BoM V-108: unit price within x5 of price_estimate_gbp | 200 | 200 | 0 | 5 | PASS | V-108 (Bürkert Type 2301): price DELIBERATELY CORRECTED by the pricing pass (£200; basis: actuated-valve assembly (actuator + valve body as ONE unit): £80 base + £1.85/DN); the parametric price_estimate_gbp £18 was rejected/superseded by that correction — banding against it is self-contradictory. |  |  | BoM V-108: unit price within x5 of price_estimate_gbp | 200 | 200 |  | 0 | BoM I-110: unit_gbp x qty == line_gbp | 12 | 12 | 1 | 0
BoM I-104: unit price within x5 of price_estimate_gbp | 12 | 12 | 0 | 5 | PASS | I-104 (Myron L 750-II-CS51): BoM unit £12 vs price_estimate_gbp £12 = x1.0. Flag when >x5 or <x0.2. |  |  | BoM I-104: unit price within x5 of price_estimate_gbp | 12 | 12 |  | 0 | BoM X-127: unit_gbp x qty == line_gbp | 691 | 691 | 1 | 0
BoM I-105: unit price within x5 of distributor_price_gbp | 691 | 691 | 0 | 5 | PASS | I-105 (Endress+Hauser DMA50-AAABA1): BoM unit £691 vs distributor_price_gbp £691 = x1.0. Flag when >x5 or <x0.2. |  |  | BoM I-105: unit price within x5 of distributor_price_gbp | 691 | 691 |  | 0 | BoM EP-102: unit_gbp x qty == line_gbp | 283 | 283 | 1 | 0
BoM I-106: unit price within x5 of price_estimate_gbp | 12 | 12 | 0 | 5 | PASS | I-106 (Endress+Hauser CPS11E): BoM unit £12 vs price_estimate_gbp £12 = x1.0. Flag when >x5 or <x0.2. |  |  | BoM I-106: unit price within x5 of price_estimate_gbp | 12 | 12 |  | 0 | BoM EP-101: unit_gbp x qty == line_gbp | 4250 | 4250 | 1 | 0
BoM I-107: unit price within x5 of price_estimate_gbp | 12 | 12 | 0 | 5 | PASS | I-107 (Endress+Hauser CPS12D): BoM unit £12 vs price_estimate_gbp £12 = x1.0. Flag when >x5 or <x0.2. |  |  | BoM I-107: unit price within x5 of price_estimate_gbp | 12 | 12 |  | 0 | BoM X-128: unit_gbp x qty == line_gbp | 219 | 219 | 1 | 0
BoM I-108: unit price within x5 of price_estimate_gbp | 280 | 280 | 0 | 5 | PASS | I-108 (Hach 5500sc): BoM unit £280 vs price_estimate_gbp £280 = x1.0. Flag when >x5 or <x0.2. |  |  | BoM I-108: unit price within x5 of price_estimate_gbp | 280 | 280 |  | 0 | BoM X-129: unit_gbp x qty == line_gbp | 250 | 250 | 1 | 0
BoM I-109: unit price within x5 of price_estimate_gbp | 12 | 12 | 0 | 5 | PASS | I-109 (Hach LXV45B.99.11022): BoM unit £12 vs price_estimate_gbp £12 = x1.0. Flag when >x5 or <x0.2. |  |  | BoM I-109: unit price within x5 of price_estimate_gbp | 12 | 12 |  | 0 | BoM X-106: unit_gbp x qty == line_gbp | 9 | 9 | 1 | 0
BoM I-110: unit price within x5 of price_estimate_gbp | 12 | 12 | 0 | 5 | PASS | I-110 (Myron L 750-II-CS51): BoM unit £12 vs price_estimate_gbp £12 = x1.0. Flag when >x5 or <x0.2. |  |  | BoM I-110: unit price within x5 of price_estimate_gbp | 12 | 12 |  | 0 | BoM X-105: unit_gbp x qty == line_gbp | 9 | 9 | 1 | 0
BoM X-127: unit price within x5 of distributor_price_gbp | 691 | 691 | 0 | 5 | PASS | X-127 (Endress+Hauser DMA50-AAABA1): BoM unit £691 vs distributor_price_gbp £691 = x1.0. Flag when >x5 or <x0.2. |  |  | BoM X-127: unit price within x5 of distributor_price_gbp | 691 | 691 |  | 0 | BoM X-130: unit_gbp x qty == line_gbp | 18 | 18 | 1 | 0
BoM EP-102: unit price within x5 of distributor_price_gbp | 283 | 283 | 0 | 5 | PASS | EP-102 (ABB 1SDA067417R1): BoM unit £283 vs distributor_price_gbp £283 = x1.0. Flag when >x5 or <x0.2. |  |  | BoM EP-102: unit price within x5 of distributor_price_gbp | 283 | 283 |  | 0 | BoM X-131: unit_gbp x qty == line_gbp | 1 | 1 | 1 | 0
BoM EP-101: unit price within x5 of price_estimate_gbp | 4250 | 4250 | 0 | 5 | PASS | EP-101 (Schneider Electric BlokSeT MB301M): BoM unit £4,250 vs price_estimate_gbp £4,250 = x1.0. Flag when >x5 or <x0.2. |  |  | BoM EP-101: unit price within x5 of price_estimate_gbp | 4250 | 4250 |  | 0 | BoM X-132: unit_gbp x qty == line_gbp | 40 | 40 | 1 | 0
BoM X-128: unit price within x5 of distributor_price_gbp | 219 | 214 | 5 | 5 | PASS | X-128 (Omron Automation and Safety S8VS-09024BP): BoM unit £219 vs distributor_price_gbp £214 = x1.0. Flag when >x5 or <x0.2. |  |  | BoM X-128: unit price within x5 of distributor_price_gbp | 219 | 214 |  | 0 | BoM F-3: unit_gbp x qty == line_gbp | 11000 | 11000 | 1 | 0
BoM X-129: unit price within x5 of price_estimate_gbp | 250 | 250.34 | -0.34 | 5 | PASS | X-129 (Phoenix Contact 2838199): BoM unit £250 vs price_estimate_gbp £250 = x1.0. Flag when >x5 or <x0.2. |  |  | BoM X-129: unit price within x5 of price_estimate_gbp | 250 | 250.34 |  | 0 | BoM X-133: unit_gbp x qty == line_gbp | 40 | 40 | 1 | 0
BoM X-130: unit price within x5 of price_estimate_gbp | 18 | 18 | 0 | 5 | PASS | X-130 (Swagelok SS-42GS4): BoM unit £18 vs price_estimate_gbp £18 = x1.0. Flag when >x5 or <x0.2. |  |  | BoM X-130: unit price within x5 of price_estimate_gbp | 18 | 18 |  | 0 | BoM X-134: unit_gbp x qty == line_gbp | 40 | 40 | 1 | 0
BoM V-109: unit price within x5 of price_estimate_gbp | 18 | 18 | 0 | 5 | PASS | V-109 (Goetze Series 851): BoM unit £18 vs price_estimate_gbp £18 = x1.0. Flag when >x5 or <x0.2. |  |  | BoM V-109: unit price within x5 of price_estimate_gbp | 18 | 18 |  | 0 | BoM X-135: unit_gbp x qty == line_gbp | 3 | 3 | 1 | 0
BoM I-111: unit price within x5 of price_estimate_gbp | 76 | 75.75 | 0.25 | 5 | PASS | I-111 (Danfoss 060-121966): BoM unit £76 vs price_estimate_gbp £76 = x1.0. Flag when >x5 or <x0.2. |  |  | BoM I-111: unit price within x5 of price_estimate_gbp | 76 | 75.75 |  | 0 | BoM TX-101: unit_gbp x qty == line_gbp | 3000 | 3000 | 1 | 0
BoM I-112: unit price within x5 of price_estimate_gbp | 76 | 75.75 | 0.25 | 5 | PASS | I-112 (Danfoss 060-310266): BoM unit £76 vs price_estimate_gbp £76 = x1.0. Flag when >x5 or <x0.2. |  |  | BoM I-112: unit price within x5 of price_estimate_gbp | 76 | 75.75 |  | 0 | BoM V-109: unit_gbp x qty == line_gbp | 18 | 18 | 1 | 0
BoM X-136: unit price within x5 of price_estimate_gbp | 40 | 35 | 5 | 5 | PASS | X-136 (Eaton 216516): BoM unit £40 vs price_estimate_gbp £35 = x1.1. Flag when >x5 or <x0.2. |  |  | BoM X-136: unit price within x5 of price_estimate_gbp | 40 | 35 |  | 0 | BoM I-111: unit_gbp x qty == line_gbp | 76 | 76 | 1 | 0
BoM X-137: unit price within x5 of price_estimate_gbp | 45 | 45 | 0 | 5 | PASS | X-137 (Legrand SRFL100G): BoM unit £45 vs price_estimate_gbp £45 = x1.0. Flag when >x5 or <x0.2. |  |  | BoM X-137: unit price within x5 of price_estimate_gbp | 45 | 45 |  | 0 | BoM I-112: unit_gbp x qty == line_gbp | 76 | 76 | 1 | 0
BoM X-138: unit price within x5 of price_estimate_gbp | 6 | 6.5 | -0.5 | 5 | PASS | X-138 (Schneider Electric LV430630): BoM unit £6 vs price_estimate_gbp £6 = x0.9. Flag when >x5 or <x0.2. |  |  | BoM X-138: unit price within x5 of price_estimate_gbp | 6 | 6.5 |  | 0 | BoM X-136: unit_gbp x qty == line_gbp | 40 | 40 | 1 | 0
BoM X-139: unit price within x5 of price_estimate_gbp | 40 | 35 | 5 | 5 | PASS | X-139 (Eaton 216516): BoM unit £40 vs price_estimate_gbp £35 = x1.1. Flag when >x5 or <x0.2. |  |  | BoM X-139: unit price within x5 of price_estimate_gbp | 40 | 35 |  | 0 | BoM I-102: unit_gbp x qty == line_gbp | 8023 | 8023 | 1 | 0
BoM I-113: unit price within x5 of price_estimate_gbp | 12 | 12 | 0 | 5 | PASS | I-113 (nVent Raychem TT-1000): BoM unit £12 vs price_estimate_gbp £12 = x1.0. Flag when >x5 or <x0.2. |  |  | BoM I-113: unit price within x5 of price_estimate_gbp | 12 | 12 |  | 0 | BoM X-137: unit_gbp x qty == line_gbp | 45 | 45 | 1 | 0
BoM X-140: unit price within x5 of distributor_price_gbp | 96 | 96 | 0 | 5 | PASS | X-140 (Siemens 3RU2126-4DB0): BoM unit £96 vs distributor_price_gbp £96 = x1.0. Flag when >x5 or <x0.2. |  |  | BoM X-140: unit price within x5 of distributor_price_gbp | 96 | 96 |  | 0 | BoM X-138: unit_gbp x qty == line_gbp | 6 | 6 | 1 | 0
BoM I-114: unit price within x5 of distributor_price_gbp | 159 | 159 | 0 | 5 | PASS | I-114 (Banner Engineering SSA-EB1PS1-02-A01): BoM unit £159 vs distributor_price_gbp £159 = x1.0. Flag when >x5 or <x0.2. |  |  | BoM I-114: unit price within x5 of distributor_price_gbp | 159 | 159 |  | 0 | BoM X-139: unit_gbp x qty == line_gbp | 40 | 40 | 1 | 0
BoM X-141: unit price within x5 of price_estimate_gbp | 2 | 2.5 | -0.5 | 5 | PASS | X-141 (Cabletec CG-M20-IP68): BoM unit £2 vs price_estimate_gbp £2 = x0.8. Flag when >x5 or <x0.2. |  |  | BoM X-141: unit price within x5 of price_estimate_gbp | 2 | 2.5 |  | 0 | BoM I-113: unit_gbp x qty == line_gbp | 12 | 12 | 1 | 0
Sigma requirementsBom.line_gbp == cover grand total | 815837 | 815837 | 0 | 8158.37 | PASS | Sum of 417 BoM line_gbp values vs parts-ledger.grand_total_gbp. |  |  | Sigma requirementsBom.line_gbp == cover grand total | 815837 | 815837 |  |  | BoM X-140: unit_gbp x qty == line_gbp | 96 | 96 | 1 | 0
[14 empty] | BoM I-114: unit_gbp x qty == line_gbp | 159 | 159 | 1 | 0
E5 · CONNECTIVITY/SPEC — out-of-spec tally & velocity limit | [13 empty] | BoM X-141: unit_gbp x qty == line_gbp | 2 | 2 | 1 | 0
Process parts with both fluid in+out (coverage >= 80%) | 1 | 0.8 | 0.2 | 0 | PASS | 14 of 14 process parts are fully connected (fluid in AND out). The connection graph is incomplete below 80% — a vessel/pump/valve with a missing feed or discharge is a topology gap. 21 concern(s) total. |  |  | Process parts with both fluid in+out (coverage >= 80%) | 0.071429 | 0.8 | 14 |  | BoM TK-102: unit_gbp x qty == line_gbp | 4000 | 4000 | 1 | 0
Instruments associated to what they measure (coverage >= 80%) | 1 | 0.8 | 0.2 | 0 | PASS | 14 of 14 instruments are wired (>=1 signal/sense association). Below 80% leaves orphan sensors not tied to the process or the control system. |  |  | Instruments associated to what they measure (coverage >= 80%) | 0.071429 | 0.8 | 14 |  | BoM TK-101: unit_gbp x qty == line_gbp | 4000 | 4000 | 1 | 0
Ledger completeness: every part shows its required input + output | 0 | 0 | 0 | 0 | PASS | 0 part(s) are missing a required connection in the authored ledger — the design is not fully connected. Each process part must show a fluid INPUT and OUTPUT (naming what it connects to/from); a powered part a power feed; an instrument a signal tie. All parts fully connected. Fix at the ledger completion (close every part's missing direction), not by inventing a render pipe. |  |  | Ledger completeness: every part shows its required input + output | 0 | 0 |  |  | BoM X-142: unit_gbp x qty == line_gbp | 9 | 9 | 1 | 0
Ledger referential integrity: every connection names a real part | 0 | 0 | 0 | 0 | PASS | 0 connection reference(s) point to a name that is not an authored part — the graph is not fully traceable. Every edge A→B must name B by its exact part name AND appear in B's inputs. All references resolve; the whole system is traceable part-to-part. |  |  | Ledger referential integrity: every connection names a real part | 0 | 0 |  |  | BoM C01: unit_gbp x qty == line_gbp | 905 | 905 | 1 | 0
Connection rows within_spec == false (tally) | 0 | 0 | 0 | 0 | PASS | 0 of 71 connection runs are out of spec (e.g. over-velocity pipe / over-voltdrop cable). All within spec. |  |  | Connection rows within_spec == false (tally) | 0 | 0 |  |  | BoM C02: unit_gbp x qty == line_gbp | 911 | 911 | 1 | 0
Worst pipe velocity <= spec limit (DN80) | 1.457 | 3 | -1.543 | 0 | PASS | DN80 carries 1.457 m/s vs its stated limit 3 m/s. Over-velocity = erosion / head loss (0 pipe specs over limit). |  |  | Worst pipe velocity <= spec limit (DN80) | 1.457 | 3 |  |  | BoM C03: unit_gbp x qty == line_gbp | 1614 | 1614 | 1 | 0
Longest connection run <= plant diagonal x 1.8 (length plausibility) | 41.8 | 61.5 | -19.7 | 0 | PASS | Longest routed run 42 m (Permeate Outlet -> Cip Tank) vs plant footprint diagonal 34 m. A run beyond ~1.8x the diagonal is not physical inside the plant envelope -> the layout is loose and its length x GBP/m cost is inflated. Fix at the placement source (cluster connected equipment), not the cost rate. |  |  | Longest connection run <= plant diagonal x 1.8 (length plausibility) | 41.8 | 61.5 |  |  | BoM C04: unit_gbp x qty == line_gbp | 975 | 975 | 1 | 0
Total connection length <= diagonal x n_runs x 1.25 | 654 | 2008 | -1354 | 0 | PASS | Total routed connection length 654 m over 47 runs vs a plausible 2008 m (diagonal 34 m x 47 runs x 1.25). A systemic overshoot means the layout strings equipment wider than the building -> inflated pipe/cable take-off. |  |  | Total connection length <= diagonal x n_runs x 1.25 | 654 | 2008 |  |  | BoM C05: unit_gbp x qty == line_gbp | 2232 | 2232 | 1 | 0
[14 empty] | BoM C06: unit_gbp x qty == line_gbp | 1443 | 1443 | 1 | 0
E6 · BRIEF — design realises each stated brief target metric (±5%) | [13 empty] | BoM C07: unit_gbp x qty == line_gbp | 1403 | 1403 | 1 | 0
Brief target met: irrigation_demand_m3_per_hr | 90 | 45 | 45 | 2.25 | PASS | Brief target irrigation_demand_m3_per_hr = 45 m3/h; design (irrigation_demand_m3_h) = 90 m3/h — the design must realise the brief target within ±5%. |  |  | Brief target met: irrigation_demand_m3_per_hr | 90 | 45 |  |  | BoM C08: unit_gbp x qty == line_gbp | 1014 | 1014 | 1 | 0
Brief target met: ro_permeate_capacity_m3_per_hr | 8 | 8 | 0 | 0.4 | PASS | Brief target ro_permeate_capacity_m3_per_hr = 8 m3/h; design (ro_permeate_capacity_m3_h) = 8 m3/h — the design must realise the brief target within ±5%. |  |  | Brief target met: ro_permeate_capacity_m3_per_hr | 8 | 8 |  |  | BoM C09: unit_gbp x qty == line_gbp | 1559 | 1559 | 1 | 0
Brief target met: ro_recovery_percent | 75 | 75 | 0 | 3.75 | PASS | Brief target ro_recovery_percent = 75 %; design (ro_recovery_percent) = 75 % — the design must realise the brief target within ±5%. |  |  | Brief target met: ro_recovery_percent | 75 | 75 |  |  | BoM C10: unit_gbp x qty == line_gbp | 1243 | 1243 | 1 | 0
Brief target met: water_storage_capacity_m3 | 120 | 120 | 0 | 6 | PASS | Brief target water_storage_capacity_m3 = 120 m3; design (water_storage_capacity_m3) = 120 m3 — the design must realise the brief target within ±5%. |  |  | Brief target met: water_storage_capacity_m3 | 120 | 120 |  |  | BoM C11: unit_gbp x qty == line_gbp | 1176 | 1176 | 1 | 0
[14 empty] | BoM C12: unit_gbp x qty == line_gbp | 601 | 601 | 1 | 0
E7 · PROVENANCE — every engineering-tool output is actually USED by the design (no stale/orphaned tool computations) | [13 empty] | BoM C13: unit_gbp x qty == line_gbp | 984 | 984 | 1 | 0
Tool output used: incident_energy_cal_cm2 | 0.741 | 0.741 | 0 | 0.015 | PASS | arc-flash:ieee-1584 incident_energy_cal_cm2=0.741 matches contract incident_energy_cal_cm2. |  |  | Tool output used: incident_energy_cal_cm2 | 0.741 | 0.741 |  |  | BoM C14: unit_gbp x qty == line_gbp | 1228 | 1228 | 1 | 0
Tool output used: ph_control_kp | 0.296 | 0.296 | 0 | 0.01 | PASS | control-systems:pid-tuning ph_control_kp=0.296464 matches contract ph_control_kp. |  |  | Tool output used: ph_control_kp | 0.296 | 0.296 |  |  | BoM C15: unit_gbp x qty == line_gbp | 826 | 826 | 1 | 0
Tool output used: main_feeder_cable_csa_mm2 | 25 | 25 | 0 | 0.5 | PASS | electrical:cable-sizing main_feeder_cable_csa_mm2=25 matches contract main_feeder_cable_csa_mm2. |  |  | Tool output used: main_feeder_cable_csa_mm2 | 25 | 25 |  |  | BoM C16: unit_gbp x qty == line_gbp | 508 | 508 | 1 | 0
Tool output used: cable_voltdrop_pct | 2.03 | 2.03 | 0 | 0.041 | PASS | electrical:cable-sizing cable_voltdrop_pct=2.03 matches contract cable_voltdrop_pct. |  |  | Tool output used: cable_voltdrop_pct | 2.03 | 2.03 |  |  | BoM C17: unit_gbp x qty == line_gbp | 1131 | 1131 | 1 | 0
Tool output used: transformer_kva | 75 | 75 | 0 | 1.5 | PASS | electrical:transformer-sizing transformer_kva=75 matches contract transformer_kva. |  |  | Tool output used: transformer_kva | 75 | 75 |  |  | BoM C18: unit_gbp x qty == line_gbp | 352 | 352 | 1 | 0
Tool output used: transformer_secondary_current_a | 108.25 | 108.25 | 0 | 2.165 | PASS | electrical:transformer-sizing transformer_secondary_current_a=108.25 matches contract transformer_secondary_current_a. |  |  | Tool output used: transformer_secondary_current_a | 108.25 | 108.25 |  |  | BoM C19: unit_gbp x qty == line_gbp | 1265 | 1265 | 1 | 0
Tool output used: uv_disinfection_throughput_m3_h | 90 | 90 | 0 | 1.8 | PASS | first-principles:disinfection uv_disinfection_throughput_m3_h=90 matches contract uv_disinfection_throughput_m3_h. |  |  | Tool output used: uv_disinfection_throughput_m3_h | 90 | 90 |  |  | BoM C20: unit_gbp x qty == line_gbp | 1033 | 1033 | 1 | 0
Tool output used: uv_disinfection_power_kw | 4.1 | 4.1 | 0 | 0.082 | PASS | first-principles:disinfection uv_disinfection_power_kw=4.1 matches contract uv_disinfection_power_kw. |  |  | Tool output used: uv_disinfection_power_kw | 4.1 | 4.1 |  |  | BoM C21: unit_gbp x qty == line_gbp | 479 | 479 | 1 | 0
Tool output used: uv_disinfection_count | 1 | 1 | 0 | 0.02 | PASS | first-principles:disinfection uv_disinfection_count=1 matches contract uv_disinfection_count. |  |  | Tool output used: uv_disinfection_count | 1 | 1 |  |  | BoM C22: unit_gbp x qty == line_gbp | 901 | 901 | 1 | 0
Tool output used: connected_electrical_load_kw | 53 | 53 | 0 | 1.06 | PASS | first-principles:electrical connected_electrical_load_kw=53 matches contract connected_electrical_load_kw. |  |  | Tool output used: connected_electrical_load_kw | 53 | 53 |  |  | BoM C23: unit_gbp x qty == line_gbp | 1032 | 1032 | 1 | 0
Tool output used: irrigation_demand_m3_h | 90 | 90 | 0 | 1.8 | PASS | first-principles:process irrigation_demand_m3_h=90 matches contract irrigation_demand_m3_h. |  |  | Tool output used: irrigation_demand_m3_h | 90 | 90 |  |  | BoM C24: unit_gbp x qty == line_gbp | 1209 | 1209 | 1 | 0
Tool output used: water_storage_capacity_m3 | 120 | 120 | 0 | 2.4 | PASS | first-principles:process water_storage_capacity_m3=120 matches contract water_storage_capacity_m3. |  |  | Tool output used: water_storage_capacity_m3 | 120 | 120 |  |  | BoM C25: unit_gbp x qty == line_gbp | 1161 | 1161 | 1 | 0
Tool output used: softener_vessel_volume_each_m3 | 1.5 | 1.5 | 0 | 0.03 | PASS | first-principles:process softener_vessel_volume_each_m3=1.5 matches contract softener_vessel_volume_each_m3. |  |  | Tool output used: softener_vessel_volume_each_m3 | 1.5 | 1.5 |  |  | BoM C26: unit_gbp x qty == line_gbp | 398 | 398 | 1 | 0
Tool output used: fertigation_dosing_capacity_m3_per_hr | 90 | 90 | 0 | 1.8 | PASS | first-principles:process fertigation_dosing_capacity_m3_per_hr=90 matches contract fertigation_dosing_capacity_m3_per_hr. |  |  | Tool output used: fertigation_dosing_capacity_m3_per_hr | 90 | 90 |  |  | BoM C27: unit_gbp x qty == line_gbp | 913 | 913 | 1 | 0
Tool output used: total_supply_demand_kw | 53 | 53 | 0 | 1.06 | PASS | first-principles:process total_supply_demand_kw=53 matches contract total_supply_demand_kw. |  |  | Tool output used: total_supply_demand_kw | 53 | 53 |  |  | BoM C28: unit_gbp x qty == line_gbp | 670 | 670 | 1 | 0
Tool output used: main_incomer_breaker_a | 106 | 106 | 0 | 2.12 | PASS | first-principles:process main_incomer_breaker_a=106 matches contract main_incomer_breaker_a. |  |  | Tool output used: main_incomer_breaker_a | 106 | 106 |  |  | BoM C29: unit_gbp x qty == line_gbp | 1051 | 1051 | 1 | 0
Tool output used: main_incomer_breaker_frame_a | 125 | 125 | 0 | 2.5 | PASS | first-principles:process main_incomer_breaker_frame_a=125 matches contract main_incomer_breaker_frame_a. |  |  | Tool output used: main_incomer_breaker_frame_a | 125 | 125 |  |  | BoM C30: unit_gbp x qty == line_gbp | 358 | 358 | 1 | 0
Tool output used: gac_filter_vessel_volume_m3 | 1.8 | 1.8 | 0 | 0.036 | PASS | first-principles:solids gac_filter_vessel_volume_m3=1.8 matches contract gac_filter_vessel_volume_m3. |  |  | Tool output used: gac_filter_vessel_volume_m3 | 1.8 | 1.8 |  |  | BoM C31: unit_gbp x qty == line_gbp | 1280 | 1280 | 1 | 0
Tool output used: gac_vessel_diameter_m | 1.359 | 1.359 | 0 | 0.027 | PASS | gac-filter:liquid-phase-sizing gac_vessel_diameter_m=1.35875 matches contract gac_vessel_diameter_m. |  |  | Tool output used: gac_vessel_diameter_m | 1.359 | 1.359 |  |  | BoM C32: unit_gbp x qty == line_gbp | 1299 | 1299 | 1 | 0
Tool output used: softener_salt_consumption_max_kg_per_regen | 46.199 | 46.199 | 0 | 0.924 | PASS | ion-exchange:softener-sizing softener_salt_consumption_max_kg_per_regen=46.1993 matches contract softener_salt_consumption_max_kg_per_regen. |  |  | Tool output used: softener_salt_consumption_max_kg_per_regen | 46.199 | 46.199 |  |  | BoM C33: unit_gbp x qty == line_gbp | 1158 | 1158 | 1 | 0
Tool output used: drain_collection_sump_volume_each_m3 | 5 | 5 | 0 | 0.1 | PASS | irrigation:ebb-flow-demand drain_collection_sump_volume_each_m3=5 matches contract drain_collection_sump_volume_each_m3. |  |  | Tool output used: drain_collection_sump_volume_each_m3 | 5 | 5 |  |  | BoM C34: unit_gbp x qty == line_gbp | 1493 | 1493 | 1 | 0
Tool output used: irrigation_pump_motor_kw | 9.653 | 9.653 | 0 | 0.193 | PASS | irrigation:pump-sizing irrigation_pump_motor_kw=9.653 matches contract irrigation_pump_motor_kw. |  |  | Tool output used: irrigation_pump_motor_kw | 9.653 | 9.653 |  |  | BoM C35: unit_gbp x qty == line_gbp | 897 | 897 | 1 | 0
Tool output used: irrigation_pump_flow_m3_h | 90 | 90 | 0 | 1.8 | PASS | irrigation:pump-sizing irrigation_pump_flow_m3_h=90 matches contract irrigation_pump_flow_m3_h. |  |  | Tool output used: irrigation_pump_flow_m3_h | 90 | 90 |  |  | BoM C36: unit_gbp x qty == line_gbp | 1004 | 1004 | 1 | 0
Tool output used: total_system_mass_kg | 1500.8 | 1500.8 | 0 | 30.016 | PASS | mass-aggregator:envelope-check total_system_mass_kg=1500.8 matches contract total_system_mass_kg. |  |  | Tool output used: total_system_mass_kg | 1500.8 | 1500.8 |  |  | BoM C37: unit_gbp x qty == line_gbp | 875 | 875 | 1 | 0
Tool output used: cloth_filter_area_m2 | 3.466 | 3.466 | 0 | 0.069 | PASS | mechanical-filtration:cloth-screen cloth_filter_area_m2=3.46572 matches contract cloth_filter_area_m2. |  |  | Tool output used: cloth_filter_area_m2 | 3.466 | 3.466 |  |  | BoM C38: unit_gbp x qty == line_gbp | 625 | 625 | 1 | 0
Tool output used: filter_hydraulic_loading_m_h | 23.083 | 23.083 | 0 | 0.462 | PASS | mechanical-filtration:cloth-screen filter_hydraulic_loading_m_h=23.0832 matches contract filter_hydraulic_loading_m_h. |  |  | Tool output used: filter_hydraulic_loading_m_h | 23.083 | 23.083 |  |  | BoM C39: unit_gbp x qty == line_gbp | 1384 | 1384 | 1 | 0
Tool output used: acid_dose_rate_ml_min | 640 | 640 | 0 | 12.8 | PASS | ph-titration:sizing acid_dose_rate_ml_min=640 matches contract acid_dose_rate_ml_min. |  |  | Tool output used: acid_dose_rate_ml_min | 640 | 640 |  |  | BoM C40: unit_gbp x qty == line_gbp | 406 | 406 | 1 | 0
Tool output used: gac_vessel_mass_kg | 600.811 | 600.811 | 0 | 12.016 | PASS | pressure-vessel:design gac_vessel_mass_kg=600.811 matches contract gac_vessel_mass_kg. |  |  | Tool output used: gac_vessel_mass_kg | 600.811 | 600.811 |  |  | BoM C41: unit_gbp x qty == line_gbp | 1296 | 1296 | 1 | 0
Tool output used: softener_vessel_mass_kg | 556.127 | 556.127 | 0 | 11.123 | PASS | pressure-vessel:design softener_vessel_mass_kg=556.127 matches contract softener_vessel_mass_kg. |  |  | Tool output used: softener_vessel_mass_kg | 556.127 | 556.127 |  |  | BoM C42: unit_gbp x qty == line_gbp | 41 | 41 | 1 | 0
Tool output used: fertigation_dosing_pump_power_kw | 7.5 | 7.5 | 0 | 0.15 | PASS | process:pump-sizing fertigation_dosing_pump_power_kw=7.5 matches contract fertigation_dosing_pump_power_kw. |  |  | Tool output used: fertigation_dosing_pump_power_kw | 7.5 | 7.5 |  |  | BoM C43: unit_gbp x qty == line_gbp | 36 | 36 | 1 | 0
Tool output used: drain_transfer_pump_power_kw | 1.923 | 1.923 | 0 | 0.038 | PASS | process:pump-sizing drain_transfer_pump_power_kw=1.923 matches contract drain_transfer_pump_power_kw. |  |  | Tool output used: drain_transfer_pump_power_kw | 1.923 | 1.923 |  |  | BoM C44: unit_gbp x qty == line_gbp | 74 | 74 | 1 | 0
Tool output used: fresh_water_storage_capacity_m3 | 40 | 40 | 0 | 0.8 | PASS | water-storage:buffer-sizing fresh_water_storage_capacity_m3=40 matches contract fresh_water_storage_capacity_m3. |  |  | Tool output used: fresh_water_storage_capacity_m3 | 40 | 40 |  |  | BoM C45: unit_gbp x qty == line_gbp | 28 | 28 | 1 | 0
Tool output used: drain_water_tank_volume_each_m3 | 40 | 40 | 0 | 0.8 | PASS | water-storage:buffer-sizing drain_water_tank_volume_each_m3=40 matches contract drain_water_tank_volume_each_m3. |  |  | Tool output used: drain_water_tank_volume_each_m3 | 40 | 40 |  |  | BoM C46: unit_gbp x qty == line_gbp | 29 | 29 | 1 | 0
Tool output used: total_water_storage_volume_m3 | 261.6 | 261.6 | 0 | 5.232 | PASS | water-storage:buffer-sizing total_water_storage_volume_m3=261.6 matches contract total_water_storage_volume_m3. |  |  | Tool output used: total_water_storage_volume_m3 | 261.6 | 261.6 |  |  | BoM C47: unit_gbp x qty == line_gbp | 102 | 102 | 1 | 0
Tool output used: ro_membrane_area_m2 | 363.6 | 363.6 | 0 | 7.272 | PASS | water-treatment-ro:sizing ro_membrane_area_m2=363.6 matches contract ro_membrane_area_m2. |  |  | Tool output used: ro_membrane_area_m2 | 363.6 | 363.6 |  |  | BoM C48: unit_gbp x qty == line_gbp | 38 | 38 | 1 | 0
Tool output used: ro_permeate_production_m3_per_hr | 8 | 8 | 0 | 0.16 | PASS | water-treatment-ro:sizing ro_permeate_production_m3_per_hr=8 matches contract ro_permeate_production_m3_per_hr. |  |  | Tool output used: ro_permeate_production_m3_per_hr | 8 | 8 |  |  | BoM C49: unit_gbp x qty == line_gbp | 121 | 121 | 1 | 0
Tool output used: estimated_capex_gbp | 115727 | 115727 | 0 | 2314.54 | PASS | water-treatment-ro:sizing estimated_capex_gbp=115727 matches contract estimated_capex_gbp. |  |  | Tool output used: estimated_capex_gbp | 115727 | 115727 |  |  | BoM C50: unit_gbp x qty == line_gbp | 74 | 74 | 1 | 0
[14 empty] | BoM C51: unit_gbp x qty == line_gbp | 91 | 91 | 1 | 0
[14 empty] | BoM C52: unit_gbp x qty == line_gbp | 112 | 112 | 1 | 0
[14 empty] | BoM C53: unit_gbp x qty == line_gbp | 125 | 125 | 1 | 0
Brief compliance — every target vs achieved vs PASS/FAIL | [13 empty] | BoM C54: unit_gbp x qty == line_gbp | 129 | 129 | 1 | 0
[14 empty] | BoM C55: unit_gbp x qty == line_gbp | 86 | 86 | 1 | 0
Brief metric | Target | Unit | Matched contract quantity | Achieved | Direction | STATUS | Note | Cell check | [5 empty] | BoM C56: unit_gbp x qty == line_gbp | 77 | 77 | 1 | 0
Irrigation demand (m³/h) | 45 | m3/h | Irrigation pump flow (m³/h) | 90 | ≥ target (meet/exceed) | PASS | brief key: irrigation_demand_m3_per_hr → contract: irrigation_pump_flow_m3_h · unit family: flow_m3h | PASS | [5 empty] | BoM C57: unit_gbp x qty == line_gbp | 920 | 920 | 1 | 0
Cultivation containers | 6000 | count | Cultivation container count | 6000 | ≥ target (meet/exceed) | PASS | brief key: cultivation_containers → contract: cultivation_container_count · unit family: count | PASS | [5 empty] | BoM C58: unit_gbp x qty == line_gbp | 3550 | 3550 | 1 | 0
Ro permeate capacity (m³/h) | 8 | m3/h | Ro permeate capacity (m³/h) | 8 | ≥ target (meet/exceed) | PASS | brief key: ro_permeate_capacity_m3_per_hr → contract: ro_permeate_capacity_m3_h · unit family: flow_m3h | PASS | [5 empty] | BoM C59: unit_gbp x qty == line_gbp | 1872 | 1872 | 1 | 0
Ro recovery (%) | 75 | % | Ro recovery (%) | 75 | ≥ target (meet/exceed) | PASS | brief key: ro_recovery_percent → contract: ro_recovery_percent | PASS | [5 empty] | BoM C60: unit_gbp x qty == line_gbp | 1308 | 1308 | 1 | 0
Water storage capacity m3 | 120 | m3 | Water storage capacity m3 | 120 | ≥ target (meet/exceed) | PASS | brief key: water_storage_capacity_m3 → contract: water_storage_capacity_m3 · unit family: volume_m3 | PASS | [5 empty] | BoM C61: unit_gbp x qty == line_gbp | 1344 | 1344 | 1 | 0
Actuated valves | 200 | count | Actuated distribution valve count | 200 | ≥ target (meet/exceed) | PASS | brief key: actuated_valves → contract: actuated_distribution_valve_count · unit family: count | PASS | [5 empty] | BoM C62: unit_gbp x qty == line_gbp | 596 | 596 | 1 | 0
[14 empty] | BoM C63: unit_gbp x qty == line_gbp | 35 | 35 | 1 | 0
Tool provenance — input → output traceability (USED / STALE / ORPHANED) | [13 empty] | BoM C64: unit_gbp x qty == line_gbp | 21 | 21 | 1 | 0
[14 empty] | BoM C65: unit_gbp x qty == line_gbp | 35 | 35 | 1 | 0
Tool | Output field | Value | Unit | Input — from | → Consumed by | Status | Cell check | [6 empty] | BoM C66: unit_gbp x qty == line_gbp | 19 | 19 | 1 | 0
arc-flash:ieee-1584 | incident_energy_cal_cm2 | 0.741 | cal/cm2 | inputs from: brief | incident_energy_cal_cm2 = 0.741 | USED | PASS | [6 empty] | BoM C67: unit_gbp x qty == line_gbp | 34 | 34 | 1 | 0
control-systems:pid-tuning | kp | 0.29646 |  | inputs from: brief | ph_control_kp = 0.296464 | USED | PASS | [6 empty] | BoM C68: unit_gbp x qty == line_gbp | 34 | 34 | 1 | 0
electrical:cable-sizing | main_feeder_cable_csa_mm2 | 25 | mm2 | inputs from: electrical:transformer-sizing + brief | main_feeder_cable_csa_mm2 = 25 | USED | PASS | [6 empty] | BoM C69: unit_gbp x qty == line_gbp | 112 | 112 | 1 | 0
electrical:cable-sizing | cable_voltdrop_pct | 2.03 | % | inputs from: electrical:transformer-sizing + brief | cable_voltdrop_pct = 2.03 | USED | PASS | [6 empty] | BoM C70: unit_gbp x qty == line_gbp | 100 | 100 | 1 | 0
electrical:transformer-sizing | transformer_kva | 75 | kVA | inputs from: brief | transformer_kva = 75 | USED | PASS | [6 empty] | BoM C71: unit_gbp x qty == line_gbp | 36 | 36 | 1 | 0
electrical:transformer-sizing | transformer_secondary_current_a | 108.25 | A | inputs from: brief | transformer_secondary_current_a = 108.25 | USED | PASS | [6 empty] | BoM X-143: unit_gbp x qty == line_gbp | 20.8 | 4451 | 214 | 0
first-principles:disinfection | uv_disinfection_throughput_m3_h | 90 | m³/h | medium-pressure UV-C reactor sized to the peak recirculated flow (= irrigation demand 90 m³/h) for Legionella control at ≈40 mJ/cm² | uv_disinfection_throughput_m3_h = 90 | USED | PASS | [6 empty] | BoM X-144: unit_gbp x qty == line_gbp | 20.8 | 5824 | 280 | 0
first-principles:disinfection | uv_disinfection_power_kw | 4.1 | kW | UV-C lamp electrical draw ≈ 0.045 kW per m³/h at the Legionella dose (90 m³/h × 0.045) | uv_disinfection_power_kw = 4.1 | USED | PASS | [6 empty] | BoM X-145: unit_gbp x qty == line_gbp | 13.2 | 109296 | 8280 | 0
first-principles:disinfection | uv_disinfection_count | 1 | off | one duty UV-C reactor on the common recirculation main (all stored/recirculated water passes it before distribution) | uv_disinfection_count = 1 | USED | PASS | [6 empty] | BoM X-146: unit_gbp x qty == line_gbp | 20.8 | 87360 | 4200 | 0
first-principles:electrical | connected_electrical_load_kw | 53 | kW | sum of pump + dosing + control loads ≈ 53 kW — a pumping/dosing plant, NOT a megawatt facility (lighting + HVAC are out of scope) | connected_electrical_load_kw = 53 | USED | PASS | [6 empty] | BoM X-147: unit_gbp x qty == line_gbp | 20.8 | 34445 | 1656 | 0
first-principles:process | irrigation_demand_m3_h | 90 | m³/h | peak irrigation demand = 45 m³/h per department × 2 departments; lock-gate HARD slot (exit 22) | irrigation_demand_m3_h = 90 | USED | PASS | [6 empty] | BoM X-148: unit_gbp x qty == line_gbp | 35.2 | 7533 | 214 | 0
first-principles:process | water_storage_capacity_m3 | 120 | m³ | total water storage = 3 galvanised tanks (1 fresh + 2 drain) × 40 m³ = 120 m³ | water_storage_capacity_m3 = 120 | USED | PASS | [6 empty] | BoM X-149: unit_gbp x qty == line_gbp | 16.4 | 7019 | 428 | 0
first-principles:process | softener_vessel_volume_each_m3 | 1.5 | m³ | glass-fibre softener vessel (350 L resin each, 14 m³/h duplex) | softener_vessel_volume_each_m3 = 1.5 | USED | PASS | [6 empty] | BoM X-150: unit_gbp x qty == line_gbp | 6 | 36000 | 6000 | 0
first-principles:process | fertigation_dosing_capacity_m3_per_hr | 90 | m³/h | total fertigation dosing capacity = 2 units × 45 m³/h = 90 m³/h | fertigation_dosing_capacity_m3_per_hr = 90 | USED | PASS | [6 empty] | BoM X-151: unit_gbp x qty == line_gbp | 9 | 27000 | 3000 | 0
first-principles:process | total_supply_demand_kw | 53 | kW | total connected electrical demand of the water plant | total_supply_demand_kw = 53 | USED | PASS | [6 empty] | BoM V-110: unit_gbp x qty == line_gbp | 40 | 8000 | 200 | 0
first-principles:process | main_incomer_breaker_a | 106 | A | main incomer sized from the connected electrical load 53 kW: I = P·1000/(√3·400·0.9)·1.25 = 106 A → next standard 125 A ACB frame | main_incomer_breaker_a = 106 | USED | PASS | [6 empty] | BoM V-111: unit_gbp x qty == line_gbp | 45 | 1980 | 44 | 0
first-principles:process | main_incomer_breaker_frame_a | 125 | A | main incomer sized from the connected electrical load 53 kW: I = P·1000/(√3·400·0.9)·1.25 = 106 A → next standard 125 A ACB frame | main_incomer_breaker_frame_a = 125 | USED | PASS | [6 empty] | BoM V-102: Sigma sub-component_gbp == line_gbp | 17540 | 17540 |  | 0
first-principles:solids | gac_filter_vessel_volume_m3 | 1.8 | m³ | granular-activated-carbon filter vessel (1 × 42-inch tank, 14.5 m³/h) | gac_filter_vessel_volume_m3 = 1.8 | USED | PASS | [6 empty] | BoM V-106: Sigma sub-component_gbp == line_gbp | 16000 | 16000 |  | 0
gac-filter:liquid-phase-sizing | gac_vessel_diameter_m | 1.3587 | m | inputs from: brief | gac_vessel_diameter_m = 1.35875 | USED | PASS | [6 empty] | BoM P-106: Sigma sub-component_gbp == line_gbp | 17268 | 17268 |  | 0
ion-exchange:softener-sizing | softener_salt_consumption_max_kg_per_regen | 46.1993 | kg | inputs from: brief | softener_salt_consumption_max_kg_per_regen = 46.1993 | USED | PASS | [6 empty] | BoM TK-103: Sigma sub-component_gbp == line_gbp | 22755 | 22752 |  | 0
irrigation:ebb-flow-demand | drain_collection_sump_volume_each_m3 | 5 | m3 | inputs from: brief | drain_collection_sump_volume_each_m3 = 5 | USED | PASS | [6 empty] | BoM P-102: Sigma sub-component_gbp == line_gbp | 2500 | 2500 |  | 0
irrigation:pump-sizing | motor_power_kw | 9.653 | kW | inputs from: irrigation:ebb-flow-demand + brief | irrigation_pump_motor_kw = 9.653 | USED | PASS | [6 empty] | BoM TK-114: Sigma sub-component_gbp == line_gbp | 9367 | 9366 |  | 0
irrigation:pump-sizing | pump_flow_m3_h | 90 | m3/h | inputs from: irrigation:ebb-flow-demand + brief | irrigation_pump_flow_m3_h = 90 | USED | PASS | [6 empty] | BoM P-104: Sigma sub-component_gbp == line_gbp | 3700 | 3700 |  | 0
mass-aggregator:envelope-check | total_system_mass_kg | 1500.8 | kg | inputs from: irrigation:pump-sizing, pressure-vessel:design + brief | total_system_mass_kg = 1500.8 | USED | PASS | [6 empty] | BoM V-104: Sigma sub-component_gbp == line_gbp | 16540 | 16540 |  | 0
mechanical-filtration:cloth-screen | cloth_filter_area_m2 | 3.4657 | m2 | inputs from: brief | cloth_filter_area_m2 = 3.46572 | USED | PASS | [6 empty] | BoM V-103: Sigma sub-component_gbp == line_gbp | 14825 | 14825 |  | 0
mechanical-filtration:cloth-screen | filter_hydraulic_loading_m_h | 23.0832 | m/h | inputs from: brief | filter_hydraulic_loading_m_h = 23.0832 | USED | PASS | [6 empty] | BoM P-103: Sigma sub-component_gbp == line_gbp | 9413 | 9413 |  | 0
ph-titration:sizing | acid_dose_rate_ml_min | 640 | mL/min | inputs from: brief | acid_dose_rate_ml_min = 640 | USED | PASS | [6 empty] | BoM Z-101: Sigma sub-component_gbp == line_gbp | 8737 | 8737 |  | 0
pressure-vessel:design | mass_kg | 600.811 | kg | inputs from: gac-filter:liquid-phase-sizing + brief | gac_vessel_mass_kg = 600.811 | USED | PASS | [6 empty] | BoM P-101: Sigma sub-component_gbp == line_gbp | 3850 | 3850 |  | 0
pressure-vessel:design | mass_kg | 556.127 | kg | inputs from: gac-filter:liquid-phase-sizing + brief | softener_vessel_mass_kg = 556.127 | USED | PASS | [6 empty] | BoM V-101: Sigma sub-component_gbp == line_gbp | 18 | 18 |  | 0
process:pump-sizing | motor_power_kw | 7.5 | kW | inputs from: brief | fertigation_dosing_pump_power_kw = 7.5 | USED | PASS | [6 empty] | BoM TK-108: Sigma sub-component_gbp == line_gbp | 13615 | 13615 |  | 0
process:pump-sizing | motor_power_kw | 1.923 | kW | inputs from: brief | drain_transfer_pump_power_kw = 1.923 | USED | PASS | [6 empty] | BoM TK-106: Sigma sub-component_gbp == line_gbp | 27231 | 27230 |  | 0
water-storage:buffer-sizing | fresh_water_storage_capacity_m3 | 40 | m3 | inputs from: irrigation:ebb-flow-demand, water-treatment-ro:sizing + brief | fresh_water_storage_capacity_m3 = 40 | USED | PASS | [6 empty] | BoM TK-102: Sigma sub-component_gbp == line_gbp | 4000 | 4000 |  | 0
water-storage:buffer-sizing | drain_water_tank_volume_each_m3 | 40 | m3 | inputs from: irrigation:ebb-flow-demand, water-treatment-ro:sizing + brief | drain_water_tank_volume_each_m3 = 40 | USED | PASS | [6 empty] | BoM TK-101: Sigma sub-component_gbp == line_gbp | 4000 | 4000 |  | 0
water-storage:buffer-sizing | total_water_storage_volume_m3 | 261.6 | m3 | inputs from: irrigation:ebb-flow-demand, water-treatment-ro:sizing + brief | total_water_storage_volume_m3 = 261.6 | USED | PASS
water-treatment-ro:sizing | ro_membrane_area_m2 | 363.6 | m2 | inputs from: brief | ro_membrane_area_m2 = 363.6 | USED | PASS
water-treatment-ro:sizing | permeate_flow_m3_h | 8 | m3/h | inputs from: brief | ro_permeate_production_m3_per_hr = 8 | USED | PASS
water-treatment-ro:sizing | estimated_capex_gbp | 115727 | GBP | inputs from: brief | estimated_capex_gbp = 115727 | USED | PASS

## Connection trace
Connection trace — which part connects to what | [5 empty] | ↑ Contents
⬤ TAB QUALITY 10/10 · PASS (target ≥8, live from the Quality & Audit score cell) · resolved-endpoint fraction (every ← / → tag must exist) + per-row status — connection rows carry a computed OK status (0 unresolved endpoints, no missing-tie evidence) 4… · full audit: Quality & Audit tab
The ledger authors every connection. INPUTS / OUTPUTS are LIVE cell-references to the connected part's own row (col A): select a cell and use Formulas ▸ Trace Precedents / Trace Dependents to draw the arrows, or click through to navigate. Each part also carries its Tag. Bidirectionally consistent. Status is a LIVE formula: OK only when every endpoint resolves to a real row/boundary AND the ledger's own completeness check is clean (columns G/H, muted).
93 authored connections · completeness: 0 part(s) missing a required tie · referential integrity: 0 broken reference(s)
Part | Tag | Status | Inputs ← (from) | Outputs → (to) | Services | Audit: unresolved endpoints (build-computed) | Audit: missing-tie evidence (build-computed) | Cell check
3 Phase Power Input | D-101 | ✓ OK | Motor Control Center | — | power | 0 |  | PASS
Chlorine Sensor | I-109 | ✓ OK | — | SCADA / Plant Control System | signal | 0 |  | PASS
Cip Tank (TK-101) | TK-101 | ✓ OK | Drain Transfer Pump, Permeate Outlet, Drain Collection Sump | Cip Tank (TK-102), Drain Collection Sump | water | 0 |  | PASS
Cip Tank (TK-102) | TK-102 | ✓ OK | Cip Tank (TK-101), Drain Collection Sump | Fresh Water Tank, Drain Collection Sump | water | 0 |  | PASS
Cloth Filter | V-104 | ✓ OK | Toray HFU-2020AN RO Membrane Elements, Motor Control Center, Drain Collection Sump | Gac Filter, Drain Collection Sump | power, water | 0 |  | PASS
Concentrate Outlet | X-105 | ✓ OK | Motor Control Center | — | power | 0 |  | PASS
Conductivity Sensor | I-104 | ✓ OK | — | SCADA / Plant Control System | signal | 0 |  | PASS
Control + Instrument UPS | U-201 | ✓ OK | Motor Control Center | Digital Control Panel | power, signal | 0 |  | PASS
Digital Control Panel | I-103 | ✓ OK | Electrical Control Panel, Control + Instrument UPS, Motor Control Center, Electrical Control Cabinet | — | power, signal | 0 |  | PASS
Distribution Manifold | M-101 | ✓ OK | Irrigation Pump | Drain Collection Sump | water | 0 |  | PASS
Distribution Transformer | TX-102 | ✓ OK | Standby Diesel Generator | Main Switchboard | power | 0 |  | PASS
Drain Collection Sump | TK-114 | ✓ OK | Uv Disinfection, Fresh Water Tank, Fertigation Dosing Pump, Nutrient Tank, Hand Watering Pump, Cloth Filter, Gac Softener, Irrigation Pump, Distribution Manifold, Reverse Osmosis Skid, Ro High Pressure Pump, Gac Filter, Uf Module Bank, Cip Tank (TK-102), Cip Tank (TK-101) | Drain Water Tank, Effluent / disposal — battery limit, Uv Disinfection, Hand Watering Pump, Cloth Filter, Gac Softener, Irrigation Pump, Reverse Osmosis Skid, Ro High Pressure Pump, Gac Filter, Uf Module Bank, Cip Tank (TK-102), Cip Tank (TK-101) | water | 0 |  | PASS
Drain Transfer Pump | P-104 | ✓ OK | Drain Water Tank, Motor Control Center, Fresh Water Tank | Cip Tank (TK-101), Effluent / disposal — battery limit | power, water | 0 |  | PASS
Drain Water Tank | TK-106 | ✓ OK | Drain Collection Sump, Fresh Water Tank | Drain Transfer Pump, Effluent / disposal — battery limit | water | 0 |  | PASS
Effluent / disposal — battery limit |  | ✓ OK | Drain Collection Sump, Drain Transfer Pump, Drain Water Tank | — | water | 0 |  | PASS
Electrical Control Cabinet | I-102 | ✓ OK | Motor Control Center | Digital Control Panel | power, signal | 0 |  | PASS
Electrical Control Panel | X-104 | ✓ OK | Motor Control Center | Digital Control Panel | power, signal | 0 |  | PASS
Fertigation Dosing Pump | P-106 | ✓ OK | Motor Control Center | Hand Watering Pump, Drain Collection Sump | power, water | 0 |  | PASS
Flow Meter (I-105) | I-105 | ✓ OK | — | SCADA / Plant Control System | signal | 0 |  | PASS
Fresh Water Tank | TK-108 | ✓ OK | Cip Tank (TK-102), Ultrafiltration Module | Nutrient Tank, Permeate Outlet, Softener Vessel, Drain Collection Sump, Drain Transfer Pump, Drain Water Tank | water | 0 |  | PASS
Gac Filter | V-101 | ✓ OK | Cloth Filter, Motor Control Center, Drain Collection Sump | Uv Disinfection, Drain Collection Sump | power, water | 0 |  | PASS
Gac Softener | V-103 | ✓ OK | Drain Collection Sump | Softener Vessel, Drain Collection Sump | water | 0 |  | PASS
Grp Membrane Housings | F-3 | ✓ OK | Softener Vessel | Uf Module Bank | water | 0 |  | PASS
Hand Watering Pump | P-102 | ✓ OK | Fertigation Dosing Pump, Motor Control Center, Drain Collection Sump | Irrigation Pump, Drain Collection Sump | power, water | 0 |  | PASS
Inlet Flow Control Valve | FCV-201–202 | ✓ OK | Softener Vessel | — | water | 0 |  | PASS
Irrigation Pump | P-103 | ✓ OK | Hand Watering Pump, Motor Control Center, Drain Collection Sump | Distribution Manifold, Drain Collection Sump | power, water | 0 |  | PASS
Leak Detection Sensor | I-113 | ✓ OK | — | SCADA / Plant Control System | signal | 0 |  | PASS
Level Transmitter | LT-201–213 | ✓ OK | — | SCADA / Plant Control System | signal | 0 |  | PASS
Main Switchboard | EP-101 | ✓ OK | Distribution Transformer | Motor Control Center | power | 0 |  | PASS
Mains Incomer | EP-102 | ✓ OK | — | Standby Diesel Generator | power | 0 |  | PASS
Motor Control Center | EP-104 | ✓ OK | Main Switchboard | Electrical Control Panel, 3 Phase Power Input, Control + Instrument UPS, SCADA / Plant Control System, Digital Control Panel, Uv Disinfection, Fertigation Dosing Pump, Hand Watering Pump, Drain Transfer Pump, Cloth Filter, Irrigation Pump, Ro High Pressure Pump, Gac Filter, Permeate Outlet, Concentrate Outlet, Electrical Control Cabinet | power, signal | 0 |  | PASS
Nutrient Tank | TK-103 | ✓ OK | Fresh Water Tank | Drain Collection Sump | water | 0 |  | PASS
Orp Sensor | I-107 | ✓ OK | — | SCADA / Plant Control System | signal | 0 |  | PASS
Permeate Outlet | X-106 | ✓ OK | Fresh Water Tank, Motor Control Center | Cip Tank (TK-101) | power, water | 0 |  | PASS
pH Analyser | AT-201 | ✓ OK | — | SCADA / Plant Control System | signal | 0 |  | PASS
Ph Sensor | I-106 | ✓ OK | — | SCADA / Plant Control System | signal | 0 |  | PASS
Pressure Transmitter | PT-201–217 | ✓ OK | — | SCADA / Plant Control System | signal | 0 |  | PASS
Reverse Osmosis Skid | Z-101 | ✓ OK | Ro High Pressure Pump, Drain Collection Sump | Toray HFU-2020AN RO Membrane Elements, Drain Collection Sump | water | 0 |  | PASS
Ro High Pressure Pump | P-101 | ✓ OK | Uf Module Bank, Motor Control Center, Drain Collection Sump | Reverse Osmosis Skid, Drain Collection Sump | power, water | 0 |  | PASS
SCADA / Plant Control System | EP-103 | ✓ OK | Conductivity Sensor, Flow Meter (I-105), Ph Sensor, Orp Sensor, Level Transmitter, pH Analyser, Pressure Transmitter, Silica Analyzer, Chlorine Sensor, Tds Sensor, Leak Detection Sensor, Motor Control Center | — | power, signal | 0 |  | PASS
Silica Analyzer | I-108 | ✓ OK | — | SCADA / Plant Control System | signal | 0 |  | PASS
Softener Vessel | V-106 | ✓ OK | Gac Softener, Fresh Water Tank | Grp Membrane Housings, Inlet Flow Control Valve, Solenoid Valve (X-124), Ultrafiltration Module | water | 0 |  | PASS
Solenoid Valve (X-124) | X-124 | ✓ OK | Softener Vessel | — | water | 0 |  | PASS
Standby Diesel Generator | G-201 | ✓ OK | Mains Incomer | Distribution Transformer | power | 0 |  | PASS
Tds Sensor | I-110 | ✓ OK | — | SCADA / Plant Control System | signal | 0 |  | PASS
Toray HFU-2020AN RO Membrane Elements | F-1 | ✓ OK | Reverse Osmosis Skid | Cloth Filter | water | 0 |  | PASS
Uf Module Bank | Z-102 | ✓ OK | Grp Membrane Housings, Drain Collection Sump | Ro High Pressure Pump, Drain Collection Sump | water | 0 |  | PASS
Ultrafiltration Module | Z-103 | ✓ OK | Softener Vessel | Fresh Water Tank | water | 0 |  | PASS
Uv Disinfection | V-102 | ✓ OK | Gac Filter, Motor Control Center, Drain Collection Sump | Drain Collection Sump | power, water | 0 |  | PASS
Cabinets — housed devices + connector proof
6 cabinet(s) · 4 housed device(s) · 1/6 cabinets fully connected · ALL CONNECTORS PROVEN: NO — see ✗ rows
SCADA / Plant Control System [CONTROL CABINET · EP-103] — 4 device(s) housed · cabinet feeds: 12 in / 0 out · ✗ INCOMPLETE
Housed device | Tag | Function | Inputs ← (from) | Outputs → (to) | Connectors | Audit: n in | Audit: n out | Cell check
Circuit Breaker | X-110 | distributes electrical power | — | — | ✗ unconnected (0 in / 0 out) | 0 | 0 | PASS
Remote Monitoring Gateway | X-123 | computes / commands | — | — | ✗ unconnected (0 in / 0 out) | 0 | 0 | PASS
Power Supply Unit | X-128 | computes / commands | — | — | ✗ unconnected (0 in / 0 out) | 0 | 0 | PASS
Surge Protection Device | X-129 | distributes electrical power | — | — | ✗ unconnected (0 in / 0 out) | 0 | 0 | PASS
Digital Control Panel [CONTROL CABINET · I-103] — 0 device(s) housed · cabinet feeds: 5 in / 0 out · ✗ INCOMPLETE
Housed device | Tag | Function | Inputs ← (from) | Outputs → (to) | Connectors | Audit: n in | Audit: n out
— no discrete devices itemised (cabinet feeds the loads directly) —
Electrical Control Panel [CONTROL CABINET · X-104] — 0 device(s) housed · cabinet feeds: 1 in / 1 out · ✓ ALL CONNECTED
Housed device | Tag | Function | Inputs ← (from) | Outputs → (to) | Connectors | Audit: n in | Audit: n out
— no discrete devices itemised (cabinet feeds the loads directly) —
PLC Controller [CONTROL CABINET · X-114] — 0 device(s) housed · cabinet feeds: 0 in / 0 out · ✗ INCOMPLETE
Housed device | Tag | Function | Inputs ← (from) | Outputs → (to) | Connectors | Audit: n in | Audit: n out
— no discrete devices itemised (cabinet feeds the loads directly) —
HMI Touchscreen [CONTROL CABINET · X-120] — 0 device(s) housed · cabinet feeds: 0 in / 0 out · ✗ INCOMPLETE
Housed device | Tag | Function | Inputs ← (from) | Outputs → (to) | Connectors | Audit: n in | Audit: n out
— no discrete devices itemised (cabinet feeds the loads directly) —
Siemens S7 1200 PLC [CONTROL CABINET · X-121] — 0 device(s) housed · cabinet feeds: 0 in / 0 out · ✗ INCOMPLETE
Housed device | Tag | Function | Inputs ← (from) | Outputs → (to) | Connectors | Audit: n in | Audit: n out
— no discrete devices itemised (cabinet feeds the loads directly) —

## Quantities
Contract inputs — traceability (where-from / where-to) | [7 empty] | ↑ Contents
⬤ TAB QUALITY 10/10 · PASS (target ≥8, live from the Quality & Audit score cell) · quantity provenance (source + where-from + used-by per row) — provenance-verified quantity rows 113/113; cell completeness+type contract 339/339 · score = min over check… · full audit: Quality & Audit tab
Where each INPUT came FROM (its source / the quantities it was computed from) and what it FEEDS into downstream. Apart from the brief, every value traces back to the briefing document. — 109/111 inputs (98%) trace to the brief.
Input | Value | Unit | Family | Source | Where-from (source / inputs) | Source detail | Used by (where-to) | Cell check
ro_permeate_capacity_m3_h | 8 | m³/h | flow_rate | brief | ← brief (stated requirement) | reverse-osmosis permeate capacity (Codema HORTI PURE RO 8 m³/h); lock-gate HARD slot (exit 22) | permeate_outlet_line_flow_m3_h, permeate_manifold_line_flow_m3_h | PASS
irrigation_demand_m3_h | 90 | m³/h | flow_rate | calculator | ← calculated (inputs in Source detail — not yet machine-linked) | peak irrigation demand = 45 m³/h per department × 2 departments; lock-gate HARD slot (exit 22) | uv_disinfection_throughput_m3_h, irrigation_pump_motor_kw, irrigation_pump_flow_m3_h | PASS
uv_disinfection_throughput_m3_h | 90 | m³/h | flow_rate | calculator | ← irrigation_demand_m3_h ✓ LIVE formula (Value is computed in-cell) | medium-pressure UV-C reactor sized to the peak recirculated flow (= irrigation demand 90 m³/h) for Legionella control at ≈40 mJ/cm² | uv_disinfection_power_kw → part: Uv Disinfection | PASS
uv_disinfection_power_kw | 4.05 | kW | power | calculator | ← uv_disinfection_throughput_m3_h ✓ LIVE formula (Value is computed in-cell) | UV-C lamp electrical draw ≈ 0.045 kW per m³/h at the Legionella dose (90 m³/h × 0.045) | → part: Uv Disinfection | PASS
uv_disinfection_count | 1 | off | count | calculator | ← measured: derived | one duty UV-C reactor on the common recirculation main (all stored/recirculated water passes it before distribution) | → part: Uv Disinfection | PASS
hand_watering_discharge_pressure_bar | 3 | bar | pressure | brief | ← brief (stated requirement) | hand-watering ring-main delivery pressure (brief-stated 3 bar; sets the hand-watering pump head) | → informs calculations / design rules (see Source detail) | PASS
fresh_water_storage_capacity_m3 | 40 | m3 | volume | brief | ← tool: water-storage:buffer-sizing | brief-pinned 40 (held — water-storage:buffer-sizing suggested 196.8: a 5× divergence, rejected as a gross override of an explicit brief spec) | → informs calculations / design rules (see Source detail) | PASS
water_storage_capacity_m3 | 120 | m³ | volume | calculator | ← fresh_water_tank_volume_each_m3, fresh_water_tank_count, drain_water_tank_count ✓ LIVE formula (Value is computed in-cell) | total water storage = 3 galvanised tanks (1 fresh + 2 drain) × 40 m³ = 120 m³ | water_storage_delivered_m3 | PASS
reverse_osmosis_skid_volume_m3 | 10 | m³ | volume | brief | ← brief (stated requirement) | reverse-osmosis packaged skid envelope (3.8 m × 1.4 m × 2.0 m, Codema HORTI PURE RO7-3LP2P, 8 m³/h @ 75% recovery) | → part: Reverse Osmosis Skid | PASS
reverse_osmosis_skid_count | 1 |  | dimensionless | brief | ← brief (stated requirement) | one RO purification skid | → part: Reverse Osmosis Skid | PASS
ro_high_pressure_pump_throughput_m3_h | 11 | m³/h | flow_rate | brief | ← brief (stated requirement) | RO frequency-controlled high-pressure pump (10.6 bar working pressure, ~10.7 m³/h feed) | pressure_vessels_line_flow_m3_h → part: Discharge Isolation Valve (on Ro High Pressure Pump), Non-Return Valve (on Ro High Pressure Pump), Ro High Pressure Pump, Suction Isolation Valve (on Ro High Pressure Pump) | PASS
ro_high_pressure_pump_power_kw | 4.2 | kW | power | brief | ← brief (stated requirement) | RO high-pressure pump motor (frequency-controlled; 4.2 kW consumption within the RO skid 5.5 kW installed) | → part: Discharge Isolation Valve (on Ro High Pressure Pump), Non-Return Valve (on Ro High Pressure Pump), Ro High Pressure Pump, Suction Isolation Valve (on Ro High Pressure Pump) | PASS
ro_high_pressure_pump_count | 1 |  | dimensionless | brief | ← brief (stated requirement) | one frequency-controlled RO high-pressure pump | → part: Discharge Isolation Valve (on Ro High Pressure Pump), Non-Return Valve (on Ro High Pressure Pump), Ro High Pressure Pump, Suction Isolation Valve (on Ro High Pressure Pump) | PASS
gac_filter_vessel_volume_m3 | 1.8 | m³ | volume | calculator | ← gac_softener_throughput_m3_h | granular-activated-carbon filter vessel (1 × 42-inch tank, 14.5 m³/h) | → informs calculations / design rules (see Source detail) | PASS
softener_vessel_volume_each_m3 | 1.5 | m³ | volume | calculator | ← calculated (inputs in Source detail — not yet machine-linked) | glass-fibre softener vessel (350 L resin each, 14 m³/h duplex) | → part: Softener Vessel | PASS
softener_vessel_count | 2 |  | dimensionless | brief | ← brief (stated requirement) | two duplex softener vessels | → part: Softener Vessel | PASS
fresh_water_tank_volume_each_m3 | 40 | m³ | volume | brief | ← brief (stated requirement) | fresh-water galvanised storage tank (3.64 m dia × 3.88 m, 40 m³) | water_storage_capacity_m3 → part: Fresh Water Tank | PASS
fresh_water_tank_count | 1 |  | dimensionless | brief | ← brief (stated requirement) | one fresh-water storage tank | water_storage_capacity_m3 → part: Fresh Water Tank | PASS
drain_water_tank_volume_each_m3 | 40 | m3 | volume | brief | ← tool: water-storage:buffer-sizing | brief-pinned 40 (held — water-storage:buffer-sizing suggested 64.8: an explicitly-dimensioned brief storage vessel is held EXACTLY (water-storage:buffer-sizing's 64.8 is a generic buffer-model refinement, rejected)) | → part: Drain Water Tank | PASS
drain_water_tank_count | 2 |  | dimensionless | brief | ← brief (stated requirement) | two drain-water storage tanks | water_storage_capacity_m3 → part: Drain Water Tank | PASS
fertigation_dosing_pump_throughput_m3_h | 45 | m³/h | flow_rate | brief | ← brief (stated requirement) | A/B fertigation circulation pump (Lowara e-SHE 50-160/75, 45 m³/h @ 3.5 bar) | fertigation_dosing_capacity_m3_per_hr, fertigation_dosing_total_m3_h → part: Discharge Isolation Valve (on Fertigation Dosing Pump), Fertigation Dosing Pump, Fertigation dosing / injection pump — vertical multistage, 30 m3/h @ 53.1 m, 7.5, Non-Return Valve (on Fertigation Dosing Pump) (+1) | PASS
fertigation_dosing_pump_power_kw | 7.5 | kW | power | brief | ← tool: process:pump-sizing | brief-pinned 7.5 (held — process:pump-sizing suggested 3.846: 3.846 < the brief 7.5 power rating — a tool must not under-size a must-meet brief spec) | connected_electrical_load_kw → part: Discharge Isolation Valve (on Fertigation Dosing Pump), Fertigation Dosing Pump, Fertigation dosing / injection pump — vertical multistage, 30 m3/h @ 53.1 m, 7.5, Non-Return Valve (on Fertigation Dosing Pump) (+1) | PASS
fertigation_dosing_pump_count | 2 |  | dimensionless | brief | ← brief (stated requirement) | 2 A/B fertigation dosing units (one per department) | fertigation_dosing_capacity_m3_per_hr, connected_electrical_load_kw → part: Discharge Isolation Valve (on Fertigation Dosing Pump), Fertigation Dosing Pump, Fertigation dosing / injection pump — vertical multistage, 30 m3/h @ 53.1 m, 7.5, Non-Return Valve (on Fertigation Dosing Pump) (+1) | PASS
fertigation_dosing_capacity_m3_per_hr | 90 | m³/h | flow_rate | calculator | ← fertigation_dosing_pump_throughput_m3_h, fertigation_dosing_pump_count ✓ LIVE formula (Value is computed in-cell) | total fertigation dosing capacity = 2 units × 45 m³/h = 90 m³/h | → part: Discharge Isolation Valve (on Fertigation Dosing Pump), Fertigation Dosing Pump, Fertigation dosing / injection pump — vertical multistage, 30 m3/h @ 53.1 m, 7.5, Non-Return Valve (on Fertigation Dosing Pump) (+1) | PASS
acid_dosing_pump_throughput_m3_h | 0.04 | m³/h | flow_rate | brief | ← brief (stated requirement) | acid metering pump (Iwaki EWN-C21VCER, 100 L barrel, ~40 L/h) | → informs calculations / design rules (see Source detail) | PASS
acid_dosing_pump_power_kw | 0.04 | kW | power | brief | ← brief (stated requirement) | acid metering pump motor (frequency-controlled) | → informs calculations / design rules (see Source detail) | PASS
acid_dosing_pump_count | 2 |  | dimensionless | brief | ← brief (stated requirement) | 2 acid dosing pumps (one per A/B fertigation unit) | → informs calculations / design rules (see Source detail) | PASS
chemical_dosing_pump_throughput_m3_h | 0.04 | m³/h | flow_rate | brief | ← brief (stated requirement) | chemical/nutrient metering pump (Iwaki EWN-C21VHERA, 100 L barrel, ~40 L/h) | → informs calculations / design rules (see Source detail) | PASS
chemical_dosing_pump_power_kw | 0.04 | kW | power | brief | ← brief (stated requirement) | chemical metering pump motor (frequency-controlled) | → informs calculations / design rules (see Source detail) | PASS
chemical_dosing_pump_count | 2 |  | dimensionless | brief | ← brief (stated requirement) | 2 chemical/nutrient dosing pumps (one per A/B fertigation unit) | → informs calculations / design rules (see Source detail) | PASS
nutrient_tank_volume_each_m3 | 1 | m³ | volume | brief | ← brief (stated requirement) | nutrient stock tank (1,000 L polyester, 4 × A + 4 × B) | → part: Nutrient Tank | PASS
nutrient_tank_count | 8 |  | dimensionless | brief | ← brief (stated requirement) | eight 1,000 L nutrient stock tanks | → part: Nutrient Tank | PASS
hand_watering_pump_throughput_m3_h | 25 | m³/h | flow_rate | brief | ← brief (stated requirement) | hand-watering frequency-controlled pump (25 m³/h @ 3 bar) | hand_watering_pump_motor_kw, hand_watering_ring_main_length_m, hand_watering_ring_main_dn_mm, hand_watering_riser_count → part: Discharge Isolation Valve (on Hand Watering Pump) (on Hand Watering Pump), Hand Watering Pump, Non-Return Valve (on Hand Watering Pump) (on Hand Watering Pump), Suction Isolation Valve (on Hand Watering Pump) (on Hand Watering Pump) | PASS
hand_watering_pump_count | 1 |  | dimensionless | brief | ← brief (stated requirement) | one hand-watering pump | connected_electrical_load_kw → part: Discharge Isolation Valve (on Hand Watering Pump) (on Hand Watering Pump), Hand Watering Pump, Non-Return Valve (on Hand Watering Pump) (on Hand Watering Pump), Suction Isolation Valve (on Hand Watering Pump) (on Hand Watering Pump) | PASS
drain_collection_sump_volume_each_m3 | 5 | m3 | volume | brief | ← tool: irrigation:ebb-flow-demand | brief-pinned 5 (held — irrigation:ebb-flow-demand suggested 600: a 120× divergence, rejected as a gross override of an explicit brief spec) | → part: Drain Collection Sump | PASS
drain_collection_sump_count | 2 |  | dimensionless | brief | ← brief (stated requirement) | 2 drain pits (one per cultivation room) | → part: Drain Collection Sump | PASS
drain_transfer_pump_throughput_m3_h | 45 | m³/h | flow_rate | brief | ← brief (stated requirement) | drain-pit submersible transfer pump (45 m³/h) | drain_manifold_line_flow_m3_h, drain_collection_sump_line_flow_m3_h → part: Discharge Isolation Valve (on Drain Transfer Pump) (on Drain Transfer Pump), Drain Transfer Pump, Non-Return Valve (on Drain Transfer Pump) (on Drain Transfer Pump), Suction Isolation Valve (on Drain Transfer Pump) (on Drain Transfer Pump) | PASS
drain_transfer_pump_count | 2 |  | dimensionless | brief | ← brief (stated requirement) | 2 submersible drain pumps | connected_electrical_load_kw → part: Discharge Isolation Valve (on Drain Transfer Pump) (on Drain Transfer Pump), Drain Transfer Pump, Non-Return Valve (on Drain Transfer Pump) (on Drain Transfer Pump), Suction Isolation Valve (on Drain Transfer Pump) (on Drain Transfer Pump) | PASS
cloth_filter_throughput_m3_h | 80 | m³/h | flow_rate | brief | ← brief (stated requirement) | drain-water cloth filter (80 m³/h) on HDPE tank, returns to drain tank | → part: Cloth Filter | PASS
cloth_filter_count | 2 |  | dimensionless | brief | ← brief (stated requirement) | 2 cloth-filter units | → part: Cloth Filter | PASS
cultivation_container_count | 6000 |  | dimensionless | brief | ← brief (stated requirement) | 6,000 ebb/flow cultivation containers (2 dept × 10 tunnels × 5 layers × 4 rows × 15) — the irrigation network sizing driver | → informs calculations / design rules (see Source detail) | PASS
actuated_distribution_valve_count | 200 |  | dimensionless | brief | ← brief (stated requirement) | 200 electrically-actuated 2.5-inch ebb/flow distribution valves (30 containers each) | distribution_main_length_m, distribution_main_dn_mm, distribution_riser_length_m, distribution_riser_dn_mm, distribution_zone_lateral_length_m, distribution_zone_lateral_dn_mm, distribution_drain_riser_length_m, distribution_drain_riser_dn_mm, distribution_drain_collection_length_m, distribution_drain_collection_dn_mm, distribution_drain_main_length_m, distribution_drain_main_dn_mm, distribution_network_length_km, distribution_zone_kits, distribution_position_connections, distribution_drain_outlet_connections, distribution_manifold_count, distribution_manifold_throughput_m3_h | PASS
distribution_delivery_groups | 2 |  | dimensionless | brief | ← brief (stated requirement) | 2 delivery departments — each A/B fertigation unit feeds its own department main (DN125 mainline per department) | distribution_branch_runs | PASS
distribution_branch_runs | 20 |  | dimensionless | brief | ← brief (stated requirement) | 10 cultivation tunnels per department × 2 departments = 20 branch (tunnel) runs | → informs calculations / design rules (see Source detail) | PASS
distribution_levels_per_branch | 5 |  | dimensionless | brief | ← brief (stated requirement) | 5 cultivation layers per tunnel — one zone valve per layer per riser | → informs calculations / design rules (see Source detail) | PASS
distribution_risers_per_branch | 2 |  | dimensionless | brief | ← brief (stated requirement) | two DN125 riser connections per cultivation tunnel (brief: "two riser connections per tunnel") | → informs calculations / design rules (see Source detail) | PASS
distribution_positions_per_zone | 30 |  | dimensionless | brief | ← brief (stated requirement) | 30 containers per actuated valve section (the flood-fill zone) | → informs calculations / design rules (see Source detail) | PASS
distribution_zone_rows | 2 |  | dimensionless | brief | ← brief (stated requirement) | each valve section feeds two rows of containers ("30 containers (two rows of 15) via a DN75 distribution line") | → informs calculations / design rules (see Source detail) | PASS
distribution_position_pitch_mm | 2760 | mm | length | brief | ← brief (stated requirement) | cultivation container length 2760 mm (container 2760 × 1290 mm) — the along-row position pitch | → informs calculations / design rules (see Source detail) | PASS
distribution_position_width_mm | 1290 | mm | length | brief | ← brief (stated requirement) | cultivation container width 1290 mm — sets the branch (tunnel) pitch across the rows | → informs calculations / design rules (see Source detail) | PASS
distribution_zone_valve_dn_mm | 65 | mm | dimension | brief | ← brief (stated requirement) | 2.5-inch electric zone valves → DN65 (the brief's stated valve bore) | → informs calculations / design rules (see Source detail) | PASS
ro_recovery_percent | 75 | % | dimensionless | brief | ← brief (stated requirement) | RO recovery factor (75%) | → design output (feeds cost / financial / drawings) | PASS
gac_softener_throughput_m3_h | 14.5 | m³/h | flow_rate | brief | ← brief (stated requirement) | GAC / softener treatment throughput (~14.5 m³/h) | gac_filter_vessel_volume_m3, softener_vessel_line_flow_m3_h → part: Gac Softener | PASS
connected_electrical_load_kw | 53 | kW | power | calculator | ← fertigation_dosing_pump_power_kw, fertigation_dosing_pump_count, hand_watering_pump_count, drain_transfer_pump_count | sum of pump + dosing + control loads ≈ 53 kW — a pumping/dosing plant, NOT a megawatt facility (lighting + HVAC are out of scope) | total_supply_demand_kw, main_incomer_breaker_a | PASS
building_out_of_scope | 1 |  | dimensionless | brief | ← brief (stated requirement) | the building, civils and cultivation rack framework are supplied by others — OUT of scope (no hall is synthesised around the water plant) | → informs calculations / design rules (see Source detail) | PASS
total_supply_demand_kw | 53 | kW | power | convergence-report | ← connected_electrical_load_kw, total_electrical_demand_kw | alias of connected_electrical_load_kw = 53 kW by construction (the tool-claimed plant load); the as-routed converged demand 54.772 kW (plant load + distribution parasitic, 3.3% off) RECONCILES within ±10% and is recorded here — the alias itself never moves | total_supply_demand_kva | PASS
incident_energy_cal_cm2 | 0.741 | cal/cm2 | area | tool:arc-flash:ieee-1584 | ← tool: arc-flash:ieee-1584 | computed by arc-flash:ieee-1584 (inputs from brief) | → design output (feeds cost / financial / drawings) | PASS
ph_control_kp | 0.29646 |  | dimensionless | tool:control-systems:pid-tuning | ← tool: control-systems:pid-tuning | computed by control-systems:pid-tuning (inputs from brief) | → informs calculations / design rules (see Source detail) | PASS
transformer_kva | 75 | kVA | power | tool:electrical:transformer-sizing | ← tool: electrical:transformer-sizing | computed by electrical:transformer-sizing (inputs from brief) | → part: Distribution Transformer, Transformer | PASS
transformer_secondary_current_a | 108.25 | A | current | tool:electrical:transformer-sizing | ← tool: electrical:transformer-sizing | computed by electrical:transformer-sizing (inputs from brief) | → part: Distribution Transformer, Transformer | PASS
main_feeder_cable_csa_mm2 | 25 | mm2 | area | tool:electrical:cable-sizing | ← tool: electrical:cable-sizing | computed by electrical:cable-sizing (inputs from brief) | → design output (feeds cost / financial / drawings) | PASS
cable_voltdrop_pct | 2.03 | % | dimensionless | tool:electrical:cable-sizing | ← tool: electrical:cable-sizing | computed by electrical:cable-sizing (inputs from brief) | → part: Cable Glands, Cable Trays | PASS
gac_vessel_diameter_m | 1.3587 | m | length | tool:gac-filter:liquid-phase-sizing | ← tool: gac-filter:liquid-phase-sizing | computed by gac-filter:liquid-phase-sizing (inputs from brief) | → design output (feeds cost / financial / drawings) | PASS
softener_salt_consumption_max_kg_per_regen | 46.1993 | kg | mass | tool:ion-exchange:softener-sizing | ← tool: ion-exchange:softener-sizing | computed by ion-exchange:softener-sizing (inputs from brief) | → informs calculations / design rules (see Source detail) | PASS
irrigation_pump_motor_kw | 9.653 | kW | power | tool:irrigation:pump-sizing | ← tool: irrigation:pump-sizing | computed by irrigation:pump-sizing from irrigation_demand_m3_h | total_system_mass_kg | PASS
irrigation_pump_flow_m3_h | 90 | m3/h | volflow | tool:irrigation:pump-sizing | ← tool: irrigation:pump-sizing | computed by irrigation:pump-sizing from irrigation_demand_m3_h | → informs calculations / design rules (see Source detail) | PASS
cloth_filter_area_m2 | 3.4657 | m2 | area | tool:mechanical-filtration:cloth-screen | ← tool: mechanical-filtration:cloth-screen | computed by mechanical-filtration:cloth-screen (inputs from brief) | → design output (feeds cost / financial / drawings) | PASS
filter_hydraulic_loading_m_h | 23.0832 | m/h | velocity | tool:mechanical-filtration:cloth-screen | ← tool: mechanical-filtration:cloth-screen | computed by mechanical-filtration:cloth-screen (inputs from brief) | → part: Fertigation dosing / injection pump — vertical multistage, 30 m3/h @ 53.1 m, 7.5 | PASS
acid_dose_rate_ml_min | 640 | mL/min | volflow | tool:ph-titration:sizing | ← tool: ph-titration:sizing | computed by ph-titration:sizing (inputs from brief) | → design output (feeds cost / financial / drawings) | PASS
gac_vessel_mass_kg | 600.811 | kg | mass | tool:pressure-vessel:design | ← tool: pressure-vessel:design | computed by pressure-vessel:design (inputs from brief) | → design output (feeds cost / financial / drawings) | PASS
total_system_mass_kg | 1500.8 | kg | mass | tool:mass-aggregator:envelope-check | ← tool: mass-aggregator:envelope-check | computed by mass-aggregator:envelope-check from irrigation_pump_motor_kw | → design output (feeds cost / financial / drawings) | PASS
ro_membrane_area_m2 | 363.6 | m2 | area | tool:water-treatment-ro:sizing | ← tool: water-treatment-ro:sizing | computed by water-treatment-ro:sizing (inputs from brief) | → design output (feeds cost / financial / drawings) | PASS
ro_permeate_production_m3_per_hr | 8 | m3/h | volflow | tool:water-treatment-ro:sizing | ← tool: water-treatment-ro:sizing | computed by water-treatment-ro:sizing (inputs from brief) | → informs calculations / design rules (see Source detail) | PASS
estimated_capex_gbp | 115727 | GBP | currency | tool:water-treatment-ro:sizing | ← tool: water-treatment-ro:sizing | computed by water-treatment-ro:sizing (inputs from brief) | → design output (feeds cost / financial / drawings) | PASS
total_water_storage_volume_m3 | 261.6 | m3 | volume | tool:water-storage:buffer-sizing | ← tool: water-storage:buffer-sizing | computed by water-storage:buffer-sizing (inputs from brief) | → informs calculations / design rules (see Source detail) | PASS
drain_transfer_pump_power_kw | 1.923 | kW | power | tool:process:pump-sizing | ← tool: process:pump-sizing | computed by process:pump-sizing (inputs from brief) | → part: Discharge Isolation Valve (on Drain Transfer Pump) (on Drain Transfer Pump), Drain Transfer Pump, Non-Return Valve (on Drain Transfer Pump) (on Drain Transfer Pump), Suction Isolation Valve (on Drain Transfer Pump) (on Drain Transfer Pump) | PASS
softener_vessel_mass_kg | 556.127 | kg | mass | tool:pressure-vessel:design | ← tool: pressure-vessel:design | computed by pressure-vessel:design (inputs from brief) | → design output (feeds cost / financial / drawings) | PASS
hand_watering_pump_motor_kw | 2.8 | kW | power | demand-coverage | ← hand_watering_pump_throughput_m3_h | demand-coverage: hydraulic motor floor P = Q·ΔP/(36·η) @ ΔP = 2.5 bar, η = 0.62, from hand_watering_pump_throughput_m3_h = 25 m³/h (a sizing-tool value always wins when present) | → informs calculations / design rules (see Source detail) | PASS
permeate_outlet_line_flow_m3_h | 8 | m3/h | flow_rate | demand-coverage | ← ro_permeate_capacity_m3_h | demand-coverage: service-line duty for Permeate Outlet = ro_permeate_capacity_m3_h (8 m³/h) — the one delivered flow in this endpoint's distinctive-token family (the duty that serves/fills/drains it) | → informs calculations / design rules (see Source detail) | PASS
drain_manifold_line_flow_m3_h | 45 | m3/h | flow_rate | demand-coverage | ← drain_transfer_pump_throughput_m3_h | demand-coverage: service-line duty for Drain Manifold = drain_transfer_pump_throughput_m3_h (45 m³/h) — the one delivered flow in this endpoint's distinctive-token family (the duty that serves/fills/drains it) | → informs calculations / design rules (see Source detail) | PASS
pressure_vessels_line_flow_m3_h | 11 | m3/h | flow_rate | demand-coverage | ← ro_high_pressure_pump_throughput_m3_h | demand-coverage: service-line duty for Pressure Vessels = ro_high_pressure_pump_throughput_m3_h (11 m³/h) — the one delivered flow in this endpoint's distinctive-token family (the duty that serves/fills/drains it) | → informs calculations / design rules (see Source detail) | PASS
permeate_manifold_line_flow_m3_h | 8 | m3/h | flow_rate | demand-coverage | ← ro_permeate_capacity_m3_h | demand-coverage: service-line duty for Permeate Manifold = ro_permeate_capacity_m3_h (8 m³/h) — the one delivered flow in this endpoint's distinctive-token family (the duty that serves/fills/drains it) | → informs calculations / design rules (see Source detail) | PASS
cleaning_tank_line_flow_m3_h | 4 | m3/h | flow_rate | demand-coverage | ← (cip one-charge rule) | demand-coverage: CIP recirculation duty — one cleaning-solution charge (2 m³, the one-charge rule: ~15% of the plant hourly design flow bounded 0.5–2 m³) turned over in 30 min → 4 m³/h service-line flow for Cleaning Tank | → informs calculations / design rules (see Source detail) | PASS
cip_tank_line_flow_m3_h | 4 | m3/h | flow_rate | demand-coverage | ← (cip one-charge rule) | demand-coverage: CIP recirculation duty — one cleaning-solution charge (2 m³, the one-charge rule: ~15% of the plant hourly design flow bounded 0.5–2 m³) turned over in 30 min → 4 m³/h service-line flow for Cip Tank | → informs calculations / design rules (see Source detail) | PASS
water_storage_delivered_m3 | 120 | m3 | volume_m3 | demand-coverage | ← water_storage_capacity_m3 | demand-coverage: DELIVERED storage total for brief metric water_storage_capacity_m3 = Fresh Water Tank 1× 40 m³ (contract quantity family) + Drain Water Tank 2× 40 m³ (contract quantity family) — sums the design's storage-vessel principals (capacity × qty), never the target echo, so a genuine shortfall stays visible | → informs calculations / design rules (see Source detail) | PASS
fertigation_dosing_total_m3_h | 90 | m3/h | flow_rate | demand-coverage | ← fertigation_dosing_pump_throughput_m3_h | demand-coverage: DELIVERED total = 45 m³/h per unit × 2 units (fertigation_dosing_pump_throughput_m3_h × fertigation_dosing_pump_count), corroborated by fertigation_dosing_capacity_m3_per_hr = 90 m³/h — the explicit system total, so no reader mistakes the per-unit figure for the delivery | → part: Discharge Isolation Valve (on Fertigation Dosing Pump), Fertigation Dosing Pump, Fertigation dosing / injection pump — vertical multistage, 30 m3/h @ 53.1 m, 7.5, Non-Return Valve (on Fertigation Dosing Pump) (+1) | PASS
distribution_main_length_m | 214 | m | length | demand-coverage | ← actuated_distribution_valve_count | parametric — not routed (zoned-delivery distribution network, engineered allowance): delivery mains (department spines) = 2 group(s) × (10 branches × 7.7 m branch pitch + 30 m plant-room stand-off) = 214 m; DN125 at 45 m³/h ≤ 1.3 m/s (surge-limited delivery main on a cycling valve network) · 200 zones (actuated_distribution_valve_count) × 30 positions/zone (6000 served positions); 2 delivery group(s); 20 branch runs × 5 level(s); fill duty 45 m³/h/group from irrigation_pump_flow_m3_h = 90 m³/h delivered ÷ 2 groups (the irrigation_demand_m3_per_hr = 45 m³/h per-group brief metric) | → design output (feeds cost / financial / drawings) | PASS
distribution_main_dn_mm | 125 | mm | dimension | demand-coverage | ← actuated_distribution_valve_count | parametric — not routed (zoned-delivery distribution network, engineered allowance): DN125 from d = √(4·Q/π·v) at the segment service velocity — see distribution_main_length_m for the run derivation | → informs calculations / design rules (see Source detail) | PASS
distribution_riser_length_m | 280 | m | length | demand-coverage | ← actuated_distribution_valve_count | parametric — not routed (zoned-delivery distribution network, engineered allowance): delivery risers = 40 risers (200 zones ÷ 5 levels) × 7 m (5 levels × 1.3 m tier pitch + 0.5 m) = 280 m; DN125 at 45 m³/h ≤ 1.3 m/s · 200 zones (actuated_distribution_valve_count) × 30 positions/zone (6000 served positions); 2 delivery group(s); 20 branch runs × 5 level(s); fill duty 45 m³/h/group from irrigation_pump_flow_m3_h = 90 m³/h delivered ÷ 2 groups (the irrigation_demand_m3_per_hr = 45 m³/h per-group brief metric) | → design output (feeds cost / financial / drawings) | PASS
distribution_riser_dn_mm | 125 | mm | dimension | demand-coverage | ← actuated_distribution_valve_count | parametric — not routed (zoned-delivery distribution network, engineered allowance): DN125 from d = √(4·Q/π·v) at the segment service velocity — see distribution_riser_length_m for the run derivation | → informs calculations / design rules (see Source detail) | PASS
distribution_zone_lateral_length_m | 8280 | m | length | demand-coverage | ← actuated_distribution_valve_count | parametric — not routed (zoned-delivery distribution network, engineered allowance): zone laterals = 200 zones × (30 positions/zone ÷ 2 rows × 2.76 m position pitch) = 200 × 41.4 m = 8280 m; DN75 at the 45 m³/h open-zone flood-fill duty ≤ 3.0 m/s (short-duration fill) · 200 zones (actuated_distribution_valve_count) × 30 positions/zone (6000 served positions); 2 delivery group(s); 20 branch runs × 5 level(s); fill duty 45 m³/h/group from irrigation_pump_flow_m3_h = 90 m³/h delivered ÷ 2 groups (the irrigation_demand_m3_per_hr = 45 m³/h per-group brief metric) | → design output (feeds cost / financial / drawings) | PASS
distribution_zone_lateral_dn_mm | 75 | mm | dimension | demand-coverage | ← actuated_distribution_valve_count | parametric — not routed (zoned-delivery distribution network, engineered allowance): DN75 from d = √(4·Q/π·v) at the segment service velocity — see distribution_zone_lateral_length_m for the run derivation | → informs calculations / design rules (see Source detail) | PASS
distribution_drain_riser_length_m | 4200 | m | length | demand-coverage | ← actuated_distribution_valve_count | parametric — not routed (zoned-delivery distribution network, engineered allowance): drain/return risers (mirror of the delivery grid) = 600 gravity drops (an outlet per 2 positions per level) × 7 m = 4200 m; DN110 gravity at 45 m³/h ≤ 1.4 m/s · 200 zones (actuated_distribution_valve_count) × 30 positions/zone (6000 served positions); 2 delivery group(s); 20 branch runs × 5 level(s); fill duty 45 m³/h/group from irrigation_pump_flow_m3_h = 90 m³/h delivered ÷ 2 groups (the irrigation_demand_m3_per_hr = 45 m³/h per-group brief metric) | → design output (feeds cost / financial / drawings) | PASS
distribution_drain_riser_dn_mm | 110 | mm | dimension | demand-coverage | ← actuated_distribution_valve_count | parametric — not routed (zoned-delivery distribution network, engineered allowance): DN110 from d = √(4·Q/π·v) at the segment service velocity — see distribution_drain_riser_length_m for the run derivation | → informs calculations / design rules (see Source detail) | PASS
distribution_drain_collection_length_m | 1656 | m | length | demand-coverage | ← actuated_distribution_valve_count | parametric — not routed (zoned-delivery distribution network, engineered allowance): drain collection lines = 2 floor lines/branch × 41.4 m × 20 branches = 1656 m; DN110 gravity ≤ 1.4 m/s · 200 zones (actuated_distribution_valve_count) × 30 positions/zone (6000 served positions); 2 delivery group(s); 20 branch runs × 5 level(s); fill duty 45 m³/h/group from irrigation_pump_flow_m3_h = 90 m³/h delivered ÷ 2 groups (the irrigation_demand_m3_per_hr = 45 m³/h per-group brief metric) | → design output (feeds cost / financial / drawings) | PASS
distribution_drain_collection_dn_mm | 110 | mm | dimension | demand-coverage | ← actuated_distribution_valve_count | parametric — not routed (zoned-delivery distribution network, engineered allowance): DN110 from d = √(4·Q/π·v) at the segment service velocity — see distribution_drain_collection_length_m for the run derivation | → informs calculations / design rules (see Source detail) | PASS
distribution_drain_main_length_m | 214 | m | length | demand-coverage | ← actuated_distribution_valve_count | parametric — not routed (zoned-delivery distribution network, engineered allowance): main drain headers = the delivery-spine mirror (214 m); DN160 at 45 m³/h ≤ 0.8 m/s part-full gravity equivalent · 200 zones (actuated_distribution_valve_count) × 30 positions/zone (6000 served positions); 2 delivery group(s); 20 branch runs × 5 level(s); fill duty 45 m³/h/group from irrigation_pump_flow_m3_h = 90 m³/h delivered ÷ 2 groups (the irrigation_demand_m3_per_hr = 45 m³/h per-group brief metric) | → design output (feeds cost / financial / drawings) | PASS
distribution_drain_main_dn_mm | 160 | mm | dimension | demand-coverage | ← actuated_distribution_valve_count | parametric — not routed (zoned-delivery distribution network, engineered allowance): DN160 from d = √(4·Q/π·v) at the segment service velocity — see distribution_drain_main_length_m for the run derivation | → informs calculations / design rules (see Source detail) | PASS
distribution_network_length_km | 14.844 | km | length | demand-coverage | ← actuated_distribution_valve_count | parametric — not routed (zoned-delivery distribution network, engineered allowance): total zoned-distribution pipework = mains 214 + risers 280 + zone laterals 8280 + drain risers 4200 + drain collection 1656 + drain mains 214 = 14844 m = 14.844 km · 200 zones (actuated_distribution_valve_count) × 30 positions/zone (6000 served positions); 2 delivery group(s); 20 branch runs × 5 level(s); fill duty 45 m³/h/group from irrigation_pump_flow_m3_h = 90 m³/h delivered ÷ 2 groups (the irrigation_demand_m3_per_hr = 45 m³/h per-group brief metric) | → informs calculations / design rules (see Source detail) | PASS
distribution_zone_kits | 200 |  | count | demand-coverage | ← actuated_distribution_valve_count | parametric — not routed (zoned-delivery distribution network, engineered allowance): one zone connection kit (valve stub-in, unions, supports) per sectioning valve = 200 | → informs calculations / design rules (see Source detail) | PASS
distribution_position_connections | 6000 |  | count | demand-coverage | ← actuated_distribution_valve_count | parametric — not routed (zoned-delivery distribution network, engineered allowance): one delivery inlet stub + fitting per served position = 6000 | → informs calculations / design rules (see Source detail) | PASS
distribution_drain_outlet_connections | 3000 |  | count | demand-coverage | ← actuated_distribution_valve_count | parametric — not routed (zoned-delivery distribution network, engineered allowance): one gravity drain outlet per 2 served positions = 3000 | → informs calculations / design rules (see Source detail) | PASS
distribution_manifold_count | 2 |  | count | demand-coverage | ← actuated_distribution_valve_count | parametric — not routed (zoned-delivery distribution network, engineered allowance): one distribution manifold station (delivery header, isolation + non-return valves, drain tie-in) per delivery group = 2 | → part: Distribution Manifold | PASS
distribution_manifold_throughput_m3_h | 45 | m3/h | flow_rate | demand-coverage | ← actuated_distribution_valve_count | parametric — not routed (zoned-delivery distribution network, engineered allowance): each distribution manifold passes its group's 45 m³/h delivery duty (irrigation_pump_flow_m3_h = 90 m³/h delivered ÷ 2 groups (the irrigation_demand_m3_per_hr = 45 m³/h per-group brief metric)) | → part: Distribution Manifold | PASS
hand_watering_ring_main_length_m | 428 | m | length | demand-coverage | ← hand_watering_pump_throughput_m3_h | parametric — not routed (zoned-delivery distribution network, engineered allowance): hand-watering ring main = 2 delivery group(s)/department(s) × 2 legs (ring out-and-return along the 107 m delivery spine, serving every branch head) = 428 m · 200 zones (actuated_distribution_valve_count) × 30 positions/zone (6000 served positions); 2 delivery group(s); 20 branch runs × 5 level(s); fill duty 45 m³/h/group from irrigation_pump_flow_m3_h = 90 m³/h delivered ÷ 2 groups (the irrigation_demand_m3_per_hr = 45 m³/h per-group brief metric) | → design output (feeds cost / financial / drawings) | PASS
hand_watering_ring_main_dn_mm | 90 | mm | dimension | demand-coverage | ← hand_watering_pump_throughput_m3_h | parametric — not routed (zoned-delivery distribution network, engineered allowance): DN90 from d = √(4·Q/π·v) at the 25 m³/h hand-watering duty (hand_watering_pump_throughput_m3_h) ≤ 1.3 m/s ring velocity — see hand_watering_ring_main_length_m for the run derivation | → informs calculations / design rules (see Source detail) | PASS
hand_watering_riser_count | 44 |  | count | demand-coverage | ← hand_watering_pump_throughput_m3_h | parametric — not routed (zoned-delivery distribution network, engineered allowance): hand-watering tap risers (each a hand valve + quick connector) = 2 per branch × 20 branches + 2 per delivery group at the plant/irrigation room (4) = 44 | → informs calculations / design rules (see Source detail) | PASS
main_incomer_breaker_a | 106 | A | current | calculator | ← connected_electrical_load_kw ✓ LIVE formula (Value is computed in-cell) | main incomer sized from the connected electrical load 53 kW: I = P·1000/(√3·400·0.9)·1.25 = 106 A → next standard 125 A ACB frame | main_incomer_breaker_frame_a → part: Mains Incomer | PASS
main_incomer_breaker_frame_a | 125 | A | current | calculator | ← main_incomer_breaker_a | main incomer sized from the connected electrical load 53 kW: I = P·1000/(√3·400·0.9)·1.25 = 106 A → next standard 125 A ACB frame | → part: Mains Incomer | PASS
softener_vessel_line_flow_m3_h | 14.5 | m3/h | flow_rate | demand-coverage | ← gac_softener_throughput_m3_h | demand-coverage: service-line duty for Softener Vessel = gac_softener_throughput_m3_h (14.5 m³/h) — the one delivered flow in this endpoint's distinctive-token family (the duty that serves/fills/drains it) | → informs calculations / design rules (see Source detail) | PASS
drain_collection_sump_line_flow_m3_h | 45 | m3/h | flow_rate | demand-coverage | ← drain_transfer_pump_throughput_m3_h | demand-coverage: service-line duty for Drain Collection Sump = drain_transfer_pump_throughput_m3_h (45 m³/h) — the one delivered flow in this endpoint's distinctive-token family (the duty that serves/fills/drains it) | → informs calculations / design rules (see Source detail) | PASS
interconnect_pipe_length_m | 1050.4 | m | derived | route-manifest | ← brief | measured routed fluid + thermal pipe length | → design output (feeds cost / financial / drawings) | PASS
total_supply_demand_kva | 75 | kVA | power | design-loop | ← total_supply_demand_kw ✓ LIVE formula (Value is computed in-cell) | incomer kVA = next standard rating ≥ load × 1.25: 53 kW × 1.25 = 66.25 kVA → 75 kVA (standard ladder 50/75/100/160/250…; kVA ≥ kW for any power factor — the assumption-free adequacy basis the deterministic check verifies) | → design output (feeds cost / financial / drawings) | PASS

## Calculations
Worked calculations — every value recomputed live + checked | [7 empty] | ↑ Contents
⬤ TAB QUALITY 10/10 · PASS (target ≥8, live from the Quality & Audit score cell) · worked-calc coverage (every definition resolves to a computed result; inputs populated) + tool-flow consumption — worked-calc definitions resolve to a computed result 13… · full audit: Quality & Audit tab
Yellow = editable input. Green col B = LIVE formula. 'Engine value' = the value the engine stored; Δ should be ~0 (inputs are display-rounded to 4 s.f.). Legacy calcs (no input map) are RECOMPUTED LIVE from their substitution and cross-checked against the engine value (col H verdict).
Shared constants (referenced by formulas below)
Constant | Value | Unit | Note | Cell check
rho | 1000 | kg/m³ | process-fluid density (median of 3 engine worked-calc input(s)) | PASS
rho_air | 1.2 | kg/m³ | air density | PASS
g | 9.8066 | m/s² | gravity | PASS
pi | 3.1416 | - | pi (use PI() in formulas) | PASS
mu | 0.001 | Pa·s | dynamic viscosity (water) | PASS
Tool data-flow — where each tool's inputs came from and where its outputs go
Each row: a tool OUTPUT, the INPUT it was computed from (— from), and where that value GOES (→ Consumed by). Status: USED/TRACED = the output flows on; ORPHANED = it appears nowhere downstream; STALE = the downstream value disagrees.
Tool | Output field | Value | Unit | Input — from | → Consumed by | Status | Cell check
arc-flash:ieee-1584 | incident_energy_cal_cm2 | 0.74138 | cal/cm2 | inputs from: brief | incident_energy_cal_cm2 = 0.741 | USED | PASS
control-systems:pid-tuning | kp | 0.29646 |  | inputs from: brief | ph_control_kp = 0.296464 | USED | PASS
electrical:cable-sizing | main_feeder_cable_csa_mm2 | 25 | mm2 | inputs from: electrical:transformer-sizing + brief | main_feeder_cable_csa_mm2 = 25 | USED | PASS
electrical:cable-sizing | cable_voltdrop_pct | 2.0297 | % | inputs from: electrical:transformer-sizing + brief | cable_voltdrop_pct = 2.03 | USED | PASS
electrical:transformer-sizing | transformer_kva | 75 | kVA | inputs from: brief | transformer_kva = 75 | USED | PASS
electrical:transformer-sizing | transformer_secondary_current_a | 108.2532 | A | inputs from: brief | transformer_secondary_current_a = 108.25 | USED | PASS
first-principles:disinfection | uv_disinfection_throughput_m3_h | 90 | m³/h | medium-pressure UV-C reactor sized to the peak recirculated flow (= irrigation demand 90 m³/h) for Legionella control at ≈40 mJ/cm² | uv_disinfection_throughput_m3_h = 90 | USED | PASS
first-principles:disinfection | uv_disinfection_power_kw | 4.1 | kW | UV-C lamp electrical draw ≈ 0.045 kW per m³/h at the Legionella dose (90 m³/h × 0.045) | uv_disinfection_power_kw = 4.1 | USED | PASS
first-principles:disinfection | uv_disinfection_count | 1 | off | one duty UV-C reactor on the common recirculation main (all stored/recirculated water passes it before distribution) | uv_disinfection_count = 1 | USED | PASS
first-principles:electrical | connected_electrical_load_kw | 53 | kW | sum of pump + dosing + control loads ≈ 53 kW — a pumping/dosing plant, NOT a megawatt facility (lighting + HVAC are out of scope) | connected_electrical_load_kw = 53 | USED | PASS
first-principles:process | irrigation_demand_m3_h | 90 | m³/h | peak irrigation demand = 45 m³/h per department × 2 departments; lock-gate HARD slot (exit 22) | irrigation_demand_m3_h = 90 | USED | PASS
first-principles:process | water_storage_capacity_m3 | 120 | m³ | total water storage = 3 galvanised tanks (1 fresh + 2 drain) × 40 m³ = 120 m³ | water_storage_capacity_m3 = 120 | USED | PASS
first-principles:process | softener_vessel_volume_each_m3 | 1.5 | m³ | glass-fibre softener vessel (350 L resin each, 14 m³/h duplex) | softener_vessel_volume_each_m3 = 1.5 | USED | PASS
first-principles:process | fertigation_dosing_capacity_m3_per_hr | 90 | m³/h | total fertigation dosing capacity = 2 units × 45 m³/h = 90 m³/h | fertigation_dosing_capacity_m3_per_hr = 90 | USED | PASS
first-principles:process | total_supply_demand_kw | 53 | kW | total connected electrical demand of the water plant | total_supply_demand_kw = 53 | USED | PASS
first-principles:process | main_incomer_breaker_a | 106 | A | main incomer sized from the connected electrical load 53 kW: I = P·1000/(√3·400·0.9)·1.25 = 106 A → next standard 125 A ACB frame | main_incomer_breaker_a = 106 | USED | PASS
first-principles:process | main_incomer_breaker_frame_a | 125 | A | main incomer sized from the connected electrical load 53 kW: I = P·1000/(√3·400·0.9)·1.25 = 106 A → next standard 125 A ACB frame | main_incomer_breaker_frame_a = 125 | USED | PASS
first-principles:solids | gac_filter_vessel_volume_m3 | 1.8 | m³ | granular-activated-carbon filter vessel (1 × 42-inch tank, 14.5 m³/h) | gac_filter_vessel_volume_m3 = 1.8 | USED | PASS
gac-filter:liquid-phase-sizing | gac_vessel_diameter_m | 1.3587 | m | inputs from: brief | gac_vessel_diameter_m = 1.35875 | USED | PASS
ion-exchange:softener-sizing | softener_salt_consumption_max_kg_per_regen | 46.2 | kg | inputs from: brief | softener_salt_consumption_max_kg_per_regen = 46.1993 | USED | PASS
irrigation:ebb-flow-demand | drain_collection_sump_volume_each_m3 | 5 | m3 | inputs from: brief | drain_collection_sump_volume_each_m3 = 5 | USED | PASS
irrigation:pump-sizing | motor_power_kw | 9.653 | kW | inputs from: irrigation:ebb-flow-demand + brief | irrigation_pump_motor_kw = 9.653 | USED | PASS
irrigation:pump-sizing | pump_flow_m3_h | 90 | m3/h | inputs from: irrigation:ebb-flow-demand + brief | irrigation_pump_flow_m3_h = 90 | USED | PASS
mass-aggregator:envelope-check | total_system_mass_kg | 1500.811 | kg | inputs from: irrigation:pump-sizing, pressure-vessel:design + brief | total_system_mass_kg = 1500.8 | USED | PASS
mechanical-filtration:cloth-screen | cloth_filter_area_m2 | 3.4657 | m2 | inputs from: brief | cloth_filter_area_m2 = 3.46572 | USED | PASS
mechanical-filtration:cloth-screen | filter_hydraulic_loading_m_h | 23.0832 | m/h | inputs from: brief | filter_hydraulic_loading_m_h = 23.0832 | USED | PASS
ph-titration:sizing | acid_dose_rate_ml_min | 640 | mL/min | inputs from: brief | acid_dose_rate_ml_min = 640 | USED | PASS
pressure-vessel:design | mass_kg | 600.811 | kg | inputs from: gac-filter:liquid-phase-sizing + brief | gac_vessel_mass_kg = 600.811 | USED | PASS
pressure-vessel:design | mass_kg | 556.127 | kg | inputs from: gac-filter:liquid-phase-sizing + brief | softener_vessel_mass_kg = 556.127 | USED | PASS
process:pump-sizing | motor_power_kw | 7.5 | kW | inputs from: brief | fertigation_dosing_pump_power_kw = 7.5 | USED | PASS
process:pump-sizing | motor_power_kw | 1.923 | kW | inputs from: brief | drain_transfer_pump_power_kw = 1.923 | USED | PASS
water-storage:buffer-sizing | fresh_water_storage_capacity_m3 | 40 | m3 | inputs from: irrigation:ebb-flow-demand, water-treatment-ro:sizing + brief | fresh_water_storage_capacity_m3 = 40 | USED | PASS
water-storage:buffer-sizing | drain_water_tank_volume_each_m3 | 40 | m3 | inputs from: irrigation:ebb-flow-demand, water-treatment-ro:sizing + brief | drain_water_tank_volume_each_m3 = 40 | USED | PASS
water-storage:buffer-sizing | total_water_storage_volume_m3 | 261.6 | m3 | inputs from: irrigation:ebb-flow-demand, water-treatment-ro:sizing + brief | total_water_storage_volume_m3 = 261.6 | USED | PASS
water-treatment-ro:sizing | ro_membrane_area_m2 | 363.6 | m2 | inputs from: brief | ro_membrane_area_m2 = 363.6 | USED | PASS
water-treatment-ro:sizing | permeate_flow_m3_h | 8 | m3/h | inputs from: brief | ro_permeate_production_m3_per_hr = 8 | USED | PASS
water-treatment-ro:sizing | estimated_capex_gbp | 115727 | GBP | inputs from: brief | estimated_capex_gbp = 115727 | USED | PASS
Worked calculations — every value recomputed live + cross-checked
Arc Flash IEEE 1584 · arc-flash:ieee-1584
Calc / input | Value (live) | Unit | Formula (text) | Engine value | Δ | Unit | Assumptions | Cell check
Incident energy (J/cm2 -> cal/cm2) |  |  | incident_energy_cal = incident_energy_j x cal_per_j |  |  |  |  | PASS
incident_energy_j | 3.102 | J/cm2 | [5 empty] | PASS
cal_per_j | 0.23901 | cal/J | [5 empty] | PASS
= result | 0.74138 | cal/cm2 | incident_energy_j x cal_per_j | 0.741 | 0.000378 | cal/cm2 | J/cm2 from the IEEE 1584-2018 empirical model (governing of full/reduced arcing-current cases) | PASS
Control Systems PID Tuning · control-systems:pid-tuning
Calc / input | Value (live) | Unit | Formula (text) | Engine value | Δ | Unit | Assumptions | Cell check
FOPTD time constant (Smith two-point fit) |  |  | tau = 1.5 x (t63 - t28) |  |  |  |  | PASS
t63 | 2.15 | s | [5 empty] | PASS
t28 | 1.06 | s | [5 empty] | PASS
= result | 1.635 | s | 1.5 x (t63 - t28) | 1.635 | 0 | s | Smith's method: 28.3% / 63.2% step-response times of the full plant | PASS
FOPTD dead time |  |  | theta = t63 - tau
t63 | 2.15 | s
tau | 1.635 | s |  |  |  |  | ↳ chained from $B$69
= result | 0.515 | s | t63 - tau | 0.515 | 0 | s | dead time from the same two-point FOPTD fit
Proportional gain (IMC PI rule) |  |  | Kp = (1 / K) x tau / (L + theta)
K | 1
tau | 1.635 | s |  |  |  |  | ↳ chained from $B$69
theta | 0.515 | s |  |  |  |  | ↳ chained from $B$74
L | 5 | s
= result | 0.29646 |  | (1 / K) x tau / (L + theta) | 0.29646 | 1.8858e-07 |  | IMC / Skogestad SIMC rule; L = the IMC lambda time-constant
Integral gain |  |  | Ki = Kp / Ti
Kp | 0.29646 | [5 empty] | ↳ chained from $B$81
Ti | 1.635 | s
= result | 0.18135 | 1/s | Kp / Ti | 0.18132 | 2.1566e-05 | 1/s | integral time Ti = 1.635 s from the IMC rule
Electrical Main Feeder Cable Sizing (BS 7671) · electrical:cable-sizing
Calc / input | Value (live) | Unit | Formula (text) | Engine value | Δ | Unit | Assumptions | Cell check
De-rated tabulated-current target |  |  | I_t = I_b / (Ca x Cg) |  |  |  |  | PASS
I_b | 108.25 | A | [5 empty] | PASS
Ca | 1 | [6 empty] | PASS
Cg | 1 | [6 empty] | PASS
= result | 108.25 | A | I_b / (Ca x Cg) | 108.25 | 0 | A | design current basis: design current (given) | PASS
Conductor cross-sectional area (standard selection) |  |  | CSA = smallest standard with ampacity x n_parallel >= I_t
I_t | 108.25 | A |  |  |  |  | ↳ chained from $B$95
n_parallel | 1
= result | 25 | mm2 | smallest standard with ampacity x n_parallel >= I_t | 25 | 0 | mm2 | copper, 90 C thermosetting, Reference Method C (clipped direct)
Volt drop |  |  | Vd = (mV/A/m) x I_b x L / (1000 x n_parallel)
mV/A/m | 1.5 | mV/A/m
I_b | 108.25 | A
L | 50 | m
n_parallel | 1
= result | 8.1188 | V | (mV/A/m) x I_b x L / (1000 x n_parallel) | 8.119 | -0.00025 | V | mV/A/m for 25 mm2 copper (BS 7671 Appendix 4)
Volt drop as percentage of nominal |  |  | Vd_pct = 100 x Vd / U_nom
Vd | 8.1188 | V |  |  |  |  | ↳ chained from $B$107
U_nom | 400 | V
= result | 2.0297 | % | 100 x Vd / U_nom | 2.03 | -0.00025 | % | BS 7671 §525 advisory ceiling 3.0% (within limit)
Electrical Distribution Transformer Sizing · electrical:transformer-sizing
Calc / input | Value (live) | Unit | Formula (text) | Engine value | Δ | Unit | Assumptions | Cell check
Apparent power demand (informational) |  |  | S_load = P / pf |  |  |  |  | PASS
P | 53 | kW | [5 empty] | PASS
pf | 0.85 | [6 empty] | PASS
= result | 62.3529 | kVA | P / pf | 62.35 | 0.0029412 | kVA | informational only — the nameplate mint below is pf-free (kVA >= kW at any pf) | PASS
Required rating (one-mint incomer rule) |  |  | S_req = P x (1 + headroom)
P | 53 | kW
headroom | 0.25
= result | 66.25 | kVA | P x (1 + headroom) | 66.25 | 0 | kVA | kVA >= load x 1.25 — assumption-free adequacy (kVA >= kW at any power factor)
Transformer nameplate (next standard rating) |  |  | S_rated = ceil_to_standard(S_req)
S_req | 66.25 | kVA |  |  |  |  | ↳ chained from $B$125
= result | 75 | kVA | ceil_to_standard(S_req) | 75 | 0 | kVA | smallest standard preferred kVA rating >= required (IEC 60076 series + the 75 kVA trade step; ladder 25/50/75/100/160/250…)
Primary line current |  |  | I = S x 1000 / (sqrt(3) x U_LL)
S | 75 | kVA
U_LL | 11000 | V
= result | 3.9365 | A | S x 1000 / (sqrt(3) x U_LL) | 3.94 | -0.0035209 | A | three-phase line current (line-to-line voltage)
Secondary line current |  |  | I = S x 1000 / (sqrt(3) x U_LL)
S | 75 | kVA
U_LL | 400 | V
= result | 108.2532 | A | S x 1000 / (sqrt(3) x U_LL) | 108.25 | 0.0031755 | A | three-phase line current (line-to-line voltage)
Liquid Phase GAC Filter Sizing · gac-filter:liquid-phase-sizing
Calc / input | Value (live) | Unit | Formula (text) | Engine value | Δ | Unit | Assumptions | Cell check
Vessel Volume |  |  | Q * (EBCT / 60) |  |  |  |  | PASS
Q | 14.5 | [6 empty] | PASS
EBCT | 10 | [6 empty] | PASS
= result | 2.4167 | m3 | Q * (EBCT / 60) | 2.4167 | 0 | m3 |  | PASS
Cross-sectional Area |  |  | Q / HLR
Q | 14.5
HLR | 10
= result | 1.45 | m2 | Q / HLR | 1.45 | 0 | m2
Vessel Diameter |  |  | sqrt(4 * A / pi)
A | 1.45
pi | 3.1416 | [5 empty] | ↳ chained from $B$9
= result | 1.3587 | m | sqrt(4 * A / pi) | 1.3587 | -1.5887e-06 | m
Ion Exchange Softener Sizing · ion-exchange:softener-sizing
Calc / input | Value (live) | Unit | Formula (text) | Engine value | Δ | Unit | Assumptions | Cell check
Hardness Removed |  |  | H_in - H_out |  |  |  |  | PASS
H_in | 15 | [6 empty] | PASS
H_out | 0.1 | [6 empty] | PASS
= result | 14.9 | dH | H_in - H_out | 14.9 | 0 | dH |  | PASS
Hardness Load |  |  | Q * H_removed * EQ_PER_M3_PER_DH * t_regen
Q | 10.7
H_removed | 14.9
EQ_PER_M3_PER_DH | 0.35665
t_regen | 6.5
= result | 369.5946 | eq | Q * H_removed * EQ_PER_M3_PER_DH * t_regen | 369.5946 | 0 | eq
Resin Volume [build-verified] |  |  | Hardness Load / RESIN_CAPACITY
formula |  |  | Hardness Load / RESIN_CAPACITY
substitution |  |  | 369.59 / 1200.0
result | 0.30799 |  |  | 0.308 | -3.8431e-06 | m3 | ✓ maths checks out (live: ¦Δ¦ ≤ 2% of the engine value)
Vessel Volume [build-verified] |  |  | Resin Volume * VESSEL_FREEBOARD_FACTOR
formula |  |  | Resin Volume * VESSEL_FREEBOARD_FACTOR
substitution |  |  | 0.3080 * 1.5
result | 0.462 |  |  | 0.46199 | 6.7353e-06 | m3 | ✓ maths checks out (live: ¦Δ¦ ≤ 2% of the engine value)
Salt Consumption [build-verified] |  |  | Resin Volume * SALT_DOSAGE
formula |  |  | Resin Volume * SALT_DOSAGE
substitution |  |  | 0.3080 * 150.0
result | 46.2 |  |  | 46.1993 | 0.00067353 | kg | ✓ maths checks out (live: ¦Δ¦ ≤ 2% of the engine value)· confirmed = design softener_salt_consumption_max_kg_per_regen
Ebb and Flow Irrigation Demand · irrigation:ebb-flow-demand
Calc / input | Value (live) | Unit | Formula (text) | Engine value | Δ | Unit | Assumptions | Cell check
Flood Volume |  |  | Container_Count * Area_per_Container * Flood_Depth |  |  |  |  | PASS
Container_Count | 6000 | [6 empty] | PASS
Area_per_Container | 2 | [6 empty] | PASS
Flood_Depth | 0.05 | [6 empty] | PASS
= result | 600 | m3 | Container_Count * Area_per_Container * Flood_Depth | 600 | 0 | m3 |  | PASS
Peak Irrigation Flow [build-verified] |  |  | Flood Volume / Flood_Time
formula |  |  | Flood Volume / Flood_Time
substitution |  |  | 600.0000 / 0.5
result | 1200 |  |  | 1200 | 0 | m3/h | ✓ maths checks out (live: ¦Δ¦ ≤ 2% of the engine value)
Drain Collection Sump Volume [build-verified] |  |  | Flood Volume * Drain_Fraction
formula |  |  | Flood Volume * Drain_Fraction
substitution |  |  | 600.0000 * 1.0
result | 600 |  |  | 600 | 0 | m3 | ✓ maths checks out (live: ¦Δ¦ ≤ 2% of the engine value)
Irrigation Pump Sizing · irrigation:pump-sizing
Calc / input | Value (live) | Unit | Formula (text) | Engine value | Δ | Unit | Assumptions | Cell check
Total system flow |  |  | flow_lpm = (demand_m3_h x 1000) / 60
demand_m3_h | 90 | m3/h | [5 empty] | PASS
= result | 1500 | L/min | (demand_m3_h x 1000) / 60 | 1500 | 0 | L/min | stated peak irrigation demand governs: 90.0 m3/h >= emitter-summed flow 6000 x 2.0 L/h = 12.0 m3/h (pump never undersized vs the demand) | PASS
Total pump head |  |  | head = static_head + friction_head + emitter_head
static_head | 5 | m
friction_head | 2.21 | m
emitter_head | 15.3 | m
= result | 22.51 | m | static_head + friction_head + emitter_head | 22.51 | 0 | m | friction_head from Hazen-Williams (C=150 PVC)
Pump hydraulic power |  |  | P_hyd = 1000 x 9.81 x (Q_m3h / 3600) x head
Q_m3h | 90 | m3/h
head | 22.51 | m |  |  |  |  | ↳ chained from $B$219
= result | 5520.5775 | W | 1000 x 9.81 x (Q_m3h / 3600) x head | 5521.7 | -1.1225 | W | P = rho x g x Q x H, water rho 1000 kg/m3, g 9.81 m/s2
Pump shaft power |  |  | P_shaft = P_hyd / pump_eff
P_hyd | 5520.5775 | W |  |  |  |  | ↳ chained from $B$224
pump_eff | 0.65
= result | 8494.9231 | W | P_hyd / pump_eff | 8495 | -0.076923 | W | drip pump efficiency 0.65 at duty point
Motor input power |  |  | P_motor = P_shaft / motor_eff
P_shaft | 8494.9231 | W |  |  |  |  | ↳ chained from $B$229
motor_eff | 0.88
= result | 9653.4091 | W | P_shaft / motor_eff | 9653.4 | 0.0090909 | W
Pipe velocity |  |  | velocity = (Q_m3h / 3600) / (pipe_area_mm2 / 1000000)
Q_m3h | 90 | m3/h
pipe_area_mm2 | 17671.5 | mm2
= result | 1.4147 | m/s | (Q_m3h / 3600) / (pipe_area_mm2 / 1000000) | 1.415 | -0.0002927 | m/s | keep < 2.5 m/s to avoid erosion / water hammer
Mass Budget Aggregator · mass-aggregator:envelope-check
Calc / input | Value (live) | Unit | Formula (text) | Engine value | Δ | Unit | Assumptions | Cell check
Total system mass |  |  | M_total = M_cells + M_transformer + M_pcs + M_racks + M_tare + M_components
M_cells | 0 | kg | [5 empty] | PASS
M_transformer | 500 | kg | [5 empty] | PASS
M_pcs | 0 | kg | [5 empty] | PASS
M_racks | 0 | kg | [5 empty] | PASS
M_tare | 0 | kg | [5 empty] | PASS
M_components | 1000.811 | kg | [5 empty] | PASS
= result | 1500.811 | kg | M_cells + M_transformer + M_pcs + M_racks + M_tare + M_components | 1500.8 | 0.011 | kg | M_racks = rack_count x rack mass each = 0 x 0 kg | PASS
Mass budget utilisation |  |  | U = M_total / M_envelope x 100
M_total | 1500.811 | kg |  |  |  |  | ↳ chained from $B$251
M_envelope |  | kg
= result |  | % | M_total / M_envelope x 100 |  |  | % | brief mass envelope from max_mass_kg_envelope
Mass budget breach (positive = over the envelope) |  |  | B = M_total - M_envelope
M_total | 1500.811 | kg |  |  |  |  | ↳ chained from $B$251
M_envelope |  | kg
= result |  | kg | M_total - M_envelope |  |  | kg
Recommended container count |  |  | N = ceil(M_total / M_envelope)
M_total | 1500.811 | kg |  |  |  |  | ↳ chained from $B$251
M_envelope |  | kg
= result |  |  | ceil(M_total / M_envelope) |  |  |  | round up: any breach forces an additional road-transportable container
Cloth/Screen Filter Sizing · mechanical-filtration:cloth-screen
Calc / input | Value (live) | Unit | Formula (text) | Engine value | Δ | Unit | Assumptions | Cell check
Hydraulic Loading Rate |  |  | 4.0 * (micron^0.4) * (20.0 / TSS)^0.5 |  |  |  |  | PASS
micron | 80 | [6 empty] | PASS
TSS | 20 | [6 empty] | PASS
= result | 23.0832 | m/h | 4.0 * (micron^0.4) * (20.0 / TSS)^0.5 | 23.0832 | 0 | m/h |  | PASS
Cloth Filter Area |  |  | Q / HLR
Q | 80
HLR | 23.0832
= result | 3.4657 | m2 | Q / HLR | 3.4657 | 0 | m2
pH Titration Sizing · ph-titration:sizing
Calc / input | Value (live) | Unit | Formula (text) | Engine value | Δ | Unit | Assumptions | Cell check
Moles of H+ needed for initial bolus |  |  | mol_H = (buffer_cap / 1000) x delta_pH x volume_l |  |  |  |  | PASS
buffer_cap | 2 | meq/L | [5 empty] | PASS
delta_pH | 1.2 | [6 empty] | PASS
volume_l | 8000 | L | [5 empty] | PASS
= result | 19.2 | mol | (buffer_cap / 1000) x delta_pH x volume_l | 19.2 | 0 | mol | buffer_cap in meq/L; divide by 1000 to convert meq to eq (= mol H+ for monoprotic) | PASS
Initial bolus volume of acid/base |  |  | initial_dose_ml = mol_H / acid_conc x 1000
mol_H | 19.2 | mol |  |  |  |  | ↳ chained from $B$288
acid_conc | 1 | mol/L
= result | 19200 | mL | mol_H / acid_conc x 1000 | 19200 | 0 | mL | Volume = moles / concentration; x 1000 converts L to mL
CO2 production rate in moles per hour |  |  | co2_mol_h = co2_g_h / 44
co2_g_h | 0 | g/h
= result | 0 | mol/h | co2_g_h / 44 | 0 | 0 | mol/h | Molar mass of CO2 = 44 g/mol
H+ generation rate from CO2 dissolution |  |  | H_plus_mol_h = co2_mol_h x 0.30
co2_mol_h | 0 | mol/h |  |  |  |  | ↳ chained from $B$297
= result | 0 | mol/h | co2_mol_h x 0.30 | 0 | 0 | mol/h | ~30% of dissolved CO2 forms H+ in bicarbonate-buffered medium at physiological pH
Uncontrolled pH swing per minute |  |  | dpH_per_min = (H_plus_mol_h / 60 x 1000) / (buffer_cap x volume_l)
H_plus_mol_h | 0 | mol/h |  |  |  |  | ↳ chained from $B$301
buffer_cap | 2 | meq/L
volume_l | 8000 | L
= result | 0 | pH/min | (H_plus_mol_h / 60 x 1000) / (buffer_cap x volume_l) | 0 | 0 | pH/min | H+ rate x 1000 converts mol to mmol (= meq for monoprotic acid)
Pressure Vessel Wall Design (hoop-stress sizing) · pressure-vessel:design
Calc / input | Value (live) | Unit | Formula (text) | Engine value | Δ | Unit | Assumptions | Cell check
Internal design pressure |  |  | p_design_mpa = p_design_barg x 0.1 |  |  |  |  | PASS
p_design_barg | 6 | barg | [5 empty] | PASS
= result | 0.6 | MPa | p_design_barg x 0.1 | 0.6 | 0 | MPa | internal gauge design pressure of the process vessel | PASS
Shell minimum thickness (hoop stress, internal pressure) |  |  | t = p_design x D / (2 x S x E - 1.2 x p_design) + corr
p_design | 0.6 | MPa
D | 1358.75 | mm
S | 137 | MPa
E | 0.85
corr | 3 | mm
= result | 6.5113 | mm | p_design x D / (2 x S x E - 1.2 x p_design) + corr | 6.5113 | 4.3484e-06 | mm | ASME VIII Div.1 UG-27 circumferential-stress form (BS EN 13445 equivalent)
Hoop stress at adopted wall (internal pressure) |  |  | sigma_hoop = p_design x D / (2 x t)
p_design | 0.6 | MPa
D | 1358.75 | mm
t | 6.5113 | mm |  |  |  |  | ↳ chained from $B$322
= result | 62.6027 | MPa | p_design x D / (2 x t) | 62.6028 | -9.3935e-05 | MPa | thin-wall cylinder under internal pressure
Yield safety factor (hoop-governing, internal pressure) |  |  | SF_yield = yield_mpa / sigma_hoop
yield_mpa | 290 | MPa
sigma_hoop | 62.6027 | MPa |  |  |  |  | ↳ chained from $B$328
= result | 4.6324 |  | yield_mpa / sigma_hoop | 4.6324 | 6.6029e-07 |  | material steel_316L; yield from datasheet/standard
Cylinder wall mass |  |  | mass = pi x (r_outer^2 - r_inner^2) x length_mm x density / 1e9
r_outer | 685.886 | mm
r_inner | 679.374 | mm
length_mm | 1800 | mm
density | 8000 | kg/m3
= result | 402.2001 | kg | pi x (r_outer^2 - r_inner^2) x length_mm x density / 1e9 | 402.156 | 0.044052 | kg | material steel_316L
Head mass (2 flat-plate heads) |  |  | mass = 2 x pi x r_outer^2 x t x density / 1e9
r_outer | 685.886 | mm
t | 6.5113 | mm |  |  |  |  | ↳ chained from $B$322
density | 8000 | kg/m3
= result | 153.9719 | kg | 2 x pi x r_outer^2 x t x density / 1e9 | 153.971 | 0.0008888 | kg | flat-head approximation (conservative vs torispherical); 2 heads
Total vessel shell mass |  |  | total_mass = mass_cylinder + mass_heads
mass_cylinder | 402.156 | kg
mass_heads | 153.971 | kg
= result | 556.127 | kg | mass_cylinder + mass_heads | 556.127 | 0 | kg
Process Centrifugal Pump Sizing · process:pump-sizing
Calc / input | Value (live) | Unit | Formula (text) | Engine value | Δ | Unit | Assumptions | Cell check
Per-pump duty flow |  |  | Q_pump = Q_total / N_parallel |  |  |  |  | PASS
Q_total | 45 | m3/h | [5 empty] | PASS
N_parallel | 2 | [6 empty] | PASS
= result | 22.5 | m3/h | Q_total / N_parallel | 22.5 | 0 | m3/h | 2 parallel pump trains share the duty; ONE pump is sized on its share (per-pump x 2 = the loop total) | PASS
Pipe velocity |  |  | V = (Q_m3h / 3600) / (pi/4 x D^2)
Q_m3h | 22.5 | m3/h
D | 0.08 | m
= result | 1.2434 | m/s | (Q_m3h / 3600) / (pi/4 x D^2) | 1.2434 | -2.0071e-06 | m/s | Q_m3h / 3600 converts m3/h to m3/s
Reynolds number |  |  | Re = rho x V x D / mu
rho | 1000 | kg/m3 |  |  |  |  | ↳ chained from $B$6
V | 1.2434 | m/s |  |  |  |  | ↳ chained from $B$364
D | 0.08 | m
mu | 0.001 | Pa.s |  |  |  |  | ↳ chained from $B$10
= result | 99472 |  | rho x V x D / mu | 99471.8 | 0.2 |  | Newtonian fluid; pipe internal bore
Darcy friction factor (Swamee-Jain) |  |  | f = 0.25 / (log10(rel_rough/3.7 + 5.74/Re^0.9))^2
rel_rough | 0.000187
Re | 99472 | [5 empty] | ↳ chained from $B$371
= result | 0.018943 |  | 0.25 / (log10(rel_rough/3.7 + 5.74/Re^0.9))^2 | 0.01895 | -6.5196e-06 |  | Swamee-Jain explicit Colebrook (turbulent)
Pipe friction head (Darcy-Weisbach) |  |  | H_friction = f x (L_eff / D) x V^2 / (2 x g)
f | 0.018943 | [5 empty] | ↳ chained from $B$376
L_eff | 115 | m
D | 0.08 | m
V | 1.2434 | m/s |  |  |  |  | ↳ chained from $B$364
g | 9.8066 | m/s2 |  |  |  |  | ↳ chained from $B$8
= result | 2.153 | m | f x (L_eff / D) x V^2 / (2 x g) | 2.147 | 0.0059539 | m | Darcy-Weisbach pipe friction (chemical-engineering standard)
Process backpressure head |  |  | H_process = backpressure_kpa x 1000 / (rho x g)
backpressure_kpa | 100 | kPa
rho | 1000 | kg/m3 |  |  |  |  | ↳ chained from $B$6
g | 9.8066 | m/s2 |  |  |  |  | ↳ chained from $B$8
= result | 10.1972 | m | backpressure_kpa x 1000 / (rho x g) | 10.197 | 0.00021412 | m | column packing + heat exchangers + filter pressure drop
Pump total dynamic head |  |  | H_total = authoritative TDH (override)
H_total_override | 20 | m
= result | 20 | m | authoritative TDH (override) | 20 | 0 | m | caller-supplied total dynamic head (static+process+friction pre-summed upstream)
Pump hydraulic power |  |  | P_hyd = rho x g x (Q_m3h / 3600) x H_total
rho | 1000 | kg/m3 |  |  |  |  | ↳ chained from $B$6
g | 9.8066 | m/s2 |  |  |  |  | ↳ chained from $B$8
Q_m3h | 22.5 | m3/h
H_total | 20 | m |  |  |  |  | ↳ chained from $B$394
= result | 1225.825 | W | rho x g x (Q_m3h / 3600) x H_total | 1225.8 | 0.025 | W | P = rho g Q H
Pump shaft power |  |  | P_shaft = P_hyd / pump_eff
P_hyd | 1225.825 | W |  |  |  |  | ↳ chained from $B$401
pump_eff | 0.75
= result | 1634.4 | W | P_hyd / pump_eff | 1634.4 | 0 | W | centrifugal pump efficiency 0.75 at duty point
Motor input power |  |  | P_motor = P_shaft / motor_eff
P_shaft | 1634.4 | W |  |  |  |  | ↳ chained from $B$406
motor_eff | 0.85
= result | 1922.8235 | W | P_shaft / motor_eff | 1922.9 | -0.076471 | W | motor efficiency 0.85; recommended frame = 3.0 kW (next standard size with 15% margin)
Water Buffer Tank Sizing · water-storage:buffer-sizing
Calc / input | Value (live) | Unit | Formula (text) | Engine value | Δ | Unit | Assumptions | Cell check
Fresh Water Storage |  |  | (irrigation_demand - ro_production) * peak_duration * safety_factor |  |  |  |  | PASS
irrigation_demand | 90 | [6 empty] | PASS
ro_production | 8 | [6 empty] | PASS
peak_duration | 2 | [6 empty] | PASS
safety_factor | 1.2 | [6 empty] | PASS
= result | 196.8 | m3 | (irrigation_demand - ro_production) * peak_duration * safety_factor | 196.8 | 0 | m3 |  | PASS
Total Drain Water Storage |  |  | (irrigation_demand * drain_fraction) * peak_duration * safety_factor
irrigation_demand | 90
drain_fraction | 0.3
peak_duration | 2
safety_factor | 1.2
= result | 64.8 | m3 | (irrigation_demand * drain_fraction) * peak_duration * safety_factor | 64.8 | 0 | m3
Water Treatment RO Sizing · water-treatment-ro:sizing
Calc / input | Value (live) | Unit | Formula (text) | Engine value | Δ | Unit | Assumptions | Cell check
Permeate flow rate |  |  | q_permeate = daily_demand / op_hours |  |  |  |  | PASS
daily_demand | 192000 | L/day | [5 empty] | PASS
op_hours | 24 | h/day | [5 empty] | PASS
= result | 8000 | L/h | daily_demand / op_hours | 8000 | 0 | L/h | system operates at constant flow rate during operating hours | PASS
Feed flow rate (accounting for recovery losses) |  |  | q_feed = q_permeate / recovery
q_permeate | 8000 | L/h |  |  |  |  | ↳ chained from $B$436
recovery | 0.75
= result | 10666.6667 | L/h | q_permeate / recovery | 10666.7 | -0.033333 | L/h | recovery target 75.0% per input
Reject (concentrate) flow rate |  |  | q_reject = q_feed - q_permeate
q_feed | 10666.6667 | L/h |  |  |  |  | ↳ chained from $B$441
q_permeate | 8000 | L/h |  |  |  |  | ↳ chained from $B$436
= result | 2666.7 | L/h | q_feed - q_permeate | 2666.7 | 0 | L/h | mass balance: feed = permeate + reject
Required membrane area |  |  | mem_area = q_permeate / flux_lmh
q_permeate | 8000 | L/h |  |  |  |  | ↳ chained from $B$436
flux_lmh | 22 | L/m2/h
= result | 363.6364 | m2 | q_permeate / flux_lmh | 363.64 | -0.0036364 | m2 | flux 22.0 L/m2/h for bw30_brackish membrane (DOW FILMTEC technical manual)
Hydraulic pump power |  |  | hyd_power = (p_op x q_feed_m3h / 36) / pump_eff
p_op | 12 | bar
q_feed_m3h | 10.6667 | m3/h
pump_eff | 0.7
= result | 5.0794 | kW | (p_op x q_feed_m3h / 36) / pump_eff | 5.0794 | -1.9048e-05 | kW | 1 bar x 1 m3/h / 36 = 0.02778 kW hydraulic (unit conversion)
Specific energy consumption |  |  | energy = hyd_power / (q_permeate / 1000)
hyd_power | 5.0794 | kW |  |  |  |  | ↳ chained from $B$457
q_permeate | 8000 | L/h |  |  |  |  | ↳ chained from $B$436
= result | 0.63492 | kWh/m3 | hyd_power / (q_permeate / 1000) | 0.635 | -7.5e-05 | kWh/m3 | q_permeate converted L/h to m3/h by dividing 1000

## Inputs & Assumptions
Inputs & Assumptions — the economics model drivers |  |  |  | ↑ Contents
⬤ TAB QUALITY 9.4/10 · PASS (target ≥8, live from the Quality & Audit score cell) · driver integrity (every input driver consumed by a live formula) — drivers referenced by a live formula somewhere 17/18; cell completeness+type contract 54/54 · score = … · full audit: Quality & Audit tab
EVERY yellow cell is editable. Engine-derived values are labelled 'from engine'; market defaults are grounded + cited in Basis. The Economics & Scenarios tabs reference these cells with LIVE formulas — edit one driver and the whole model + every chart recomputes.
Driver | Value | Unit | Basis / source | Cell check
Output volume (output) | 45 | m3/h | from engine · primary output metric | PASS
Sale price (per output unit) | 0 | £/m3/h | UNVERIFIED — no per-unit market price is derivable for this class. Enter a real sale price to make the economics tabs meaningful; until then revenue / EBITDA / IRR are not valid. | PASS
Consumables price (dosing chemicals · nutrient / fertiliser stock · filter media & membranes) | 0 | £/m3/h | consumable classes derived from the plant's own process/media BoM + contract lines — what it ACTUALLY consumes (not a 'feedstock'); enter a real £ per output unit to price them (0 until priced — meanwhile carried inside 'Other opex') | PASS
Consumable intensity ratio | 0 | ratio | consumable units per output unit (multiplies the consumables price above); 0 until priced | PASS
Energy price | 0.15 | £/kWh | assumed — UK industrial electricity ~£0.15/kWh (edit to your tariff) | PASS
Connected electrical load | 53 | kW | from engine · connected_electrical_load_kw | PASS
Electrical load factor | 0.65 | avg/peak | assumed average/peak electrical load factor — supply a class duty-cycle to refine | PASS
Operating hours | 8000 | h/yr | assumed — typical process-plant annual operating hours (supply a class duty-cycle to refine) | PASS
Design process flow (peak) | 90 | m³/h | from engine · largest process-flow quantity (the PEAK simultaneous demand); the Financial model's annual-delivered-volume divisor references this cell LIVE — edit it and the levelised £/m³ recomputes | PASS
Water utilisation (delivered ÷ design flow) | 0.25 | fraction | multiplies the design flow above · assumed — the design flow is the PEAK simultaneous demand, so annual delivered volume = design flow × 8760 h × this factor. 0.25 models an intermittent, demand-driven duty (sequenced valve sections / batch draw-off deliver ≈25% of the peak run continuously); set ≈0.9 for a continuous process duty, or edit to metered annual demand ÷ (design flow × 8760). Drives the levelised £/m³ on the Financial model — the electrical load factor above sizes the ENERGY line only. | PASS
Labour | 25000 | £/yr | assumed — supply a real figure. No operating headcount signal, so this is defaulted as an UNMANNED / skid plant: ~£25,000/yr for remote monitoring + periodic maintenance visits (NOT a % of capex). Enter your real annual labour cost, or supply an operating headcount. | PASS
Maintenance | 3 | % capex/yr | process-plant norm | PASS
Other opex | 27212 | £/yr | assumed — 2% of installed capex/yr (consumables, insurance, overhead; supply a class opex model to refine) | PASS
Installed capex | 1360613 | £ | from engine · costStack.installed_asp_gbp (BoM + assembly + install) | PASS
Scaling exponent n (capex ∝ output^n) | 1 | n | 1.0 = LINEAR — a MODULAR plant scaled by replicating identical units (more tanks/pumps/skids); capex per output unit is constant, de-risked + testable at small scale (the ForgeOS default for modular plant). 0.6 = the six-tenths law for MONOLITHIC equipment that scales by getting bigger. Edit to model either regime — every capex/economics cell on the sweep + solver recomputes live off this. | PASS
Discount rate | 10 | % | real WACC for a small infrastructure project | PASS
Investor hurdle rate (IRR) | 15 | % | the minimum IRR an investor demands before deploying capital — the 'investable' bar on the Investment Analysis tab; edit to your fund's threshold | PASS
Project life | 20 | yr | asset economic life for the NPV horizon | PASS

## Part names
Part names — the master list |  |  |  |  | ↑ Contents
⬤ TAB QUALITY 9.6/10 · PASS (target ≥8, live from the Quality & Audit score cell) · dedupe + completeness (every BoM tag present exactly once) + cross-link + MPN/status coverage (parts-ledger.json) — part tags unique (each physical thing named once) 93/… · full audit: Quality & Audit tab
THE single source of every part's name. Each name is typed ONCE here; every other tab (BoM, Cost, Spec sheets, Connection trace, schedules) REFERENCES these cells, never repeats the string — edit a name here and it updates across the whole workbook. Select a Name cell and use Formulas ▸ Trace Dependents to see everywhere it is used. One row per principal part; sub-components are listed under their parent on the BoM. MPN / status live-looks-up this tag's manufacturer part number (or its honest TBD status) from the Bill of Materials ledger.
Tag | Name | Qty | Requirement (as stated) | MPN / status | Cell check
X-142 | 3 Part Union Fittings | 1 | 3 Part Union Fittings | commodity — MPN at procurement | PASS
D-101 | 3 Phase Power Input | 1 | 3 Phase Power Input | TDK-Lambda DRB240-24-3-A0 | PASS
X-141 | Cable Glands | 1 | Cable Glands | Cabletec CG-M20-IP68 | PASS
X-137 | Cable Trays | 1 | Cable Trays | Legrand SRFL100G | PASS
I-109 | Chlorine Sensor | 1 | Chlorine Sensor | Hach LXV45B.99.11022 | PASS
TK-102 / TK-101 | Cip Tank | 2 | Cip Tank · 1.4 m dia x 1.3 m · MERGED ROWS (synonym): 'Cleaning Tank' (TK-102) + 'Cip Tank' (TK-101) | — not yet in ledger | PASS
X-107 / X-110 | Circuit Breaker | 2 | Circuit Breaker · MERGED ROWS (singular/plural): 'Circuit Breakers' (X-107) + 'Circuit Breaker' (X-110) | — not yet in ledger | PASS
V-104 | Cloth Filter | 2 | Cloth Filter · 80 m³/h · 3 m² area | bespoke fabrication to drawing — see sizing basis | PASS
X-113 | Compartment Spacers | 1 | Compartment Spacers | commodity — MPN at procurement | PASS
X-105 | Concentrate Outlet | 1 | Concentrate Outlet | commodity — MPN at procurement | PASS
I-104 | Conductivity Sensor | 1 | Conductivity Sensor | Myron L 750-II-CS51 | PASS
U-201 | Control + Instrument UPS | 1 | Control + Instrument UPS · 5 kW (30 min) · 600x510x660 mm | Eaton 9SX5KI | PASS
X-109 | DC Power Cabling | 1 | DC Power Cabling | commodity — MPN at procurement | PASS
X-119 | Dc3 Power Controller | 1 | Dc3 Power Controller | OEM-proprietary (no public MPN) | PASS
I-103 | Digital Control Panel | 1 | Digital Control Panel | Siemens 6AV2123-2GB03-0AX0 | PASS
M-101 | Distribution Manifold | 2 | Distribution Manifold · 45 m³/h · 700x595x770 mm | bespoke fabrication to drawing — see sizing basis | PASS
TX-102 | Distribution Transformer | 1 | Distribution Transformer · 75 kVA | Hammond Power Solutions SG3A0075KB | PASS
TK-114 | Drain Collection Sump | 2 | Drain Collection Sump · 2.1 m dia x 1.4 m | bespoke fabrication to drawing — see sizing basis | PASS
P-104 | Drain Transfer Pump | 2 | Drain Transfer Pump · 2 kW · 600x510x660 mm | Grundfos SL1.50.65.22.2.50D.C | PASS
TK-106 | Drain Water Tank | 2 | Drain Water Tank · 3.7 m dia x 3.7 m | bespoke fabrication to drawing — see sizing basis | PASS
I-102 | Electrical Control Cabinet | 1 | Electrical Control Cabinet | Rittal VX25 8284.500 | PASS
X-104 | Electrical Control Panel | 1 | Electrical Control Panel | Rittal 1180.000 | PASS
X-136 / X-139 | Emergency Stop | 2 | Emergency Stop · MERGED ROWS (synonym): 'Emergency Stop Button' (X-136) + 'Emergency Stop' (X-139) | — not yet in ledger | PASS
I-114 | Emergency Stop Switch | 1 | Emergency Stop Switch | Banner Engineering SSA-EB1PS1-02-A01 | PASS
X-117 | Ethernet Ip Module | 1 | Ethernet Ip Module | HMS Networks AB7072-B | PASS
P-106 | Fertigation Dosing Pump | 2 | Fertigation Dosing Pump · 8 kW · 600x510x660 mm | Grundfos 96122012 | PASS
X-131 | Flexmount Connectors | 1 | Flexmount Connectors | commodity — MPN at procurement | PASS
X-126 | Flow Control Valves | 1 | Flow Control Valves | Pentair Fleck 2900S | PASS
I-105 / X-127 | Flow Meter | 2 | Flow Meter · MERGED ROWS (singular/plural): 'Flow Meter' (I-105) + 'Flow Meters' (X-127) | — not yet in ledger | PASS
TK-108 | Fresh Water Tank | 1 | Fresh Water Tank · 3.7 m dia x 3.7 m | bespoke fabrication to drawing — see sizing basis | PASS
V-101 | Gac Filter | 1 | Gac Filter · 1.3 m dia x 1.4 m | General Carbon HP-1000 | PASS
V-103 | Gac Softener | 1 | Gac Softener · 15 m³/h · 0.9 m dia x 1.8 m | Pentair Structural 36X72 COMP 6"TF 6"BF | PASS
F-3 | Grp Membrane Housings | 1 | Grp Membrane Housings · 364 m² area | bespoke fabrication to drawing — see sizing basis | PASS
P-102 | Hand Watering Pump | 1 | Hand Watering Pump · 25 m³/h · 900x500x700 mm | Grundfos 96935501 | PASS
X-149 | Hand watering — ring main to both departments | 428 | Hand watering — ring main to both departments · DN90 PVC-U · 428 m | DN90 PVC-U pressure pipe + fittings + hangers, 428 m (supply) | PASS
I-112 | High Pressure Switch | 1 | High Pressure Switch | Danfoss 060-310266 | PASS
X-120 | HMI Touchscreen | 1 | HMI Touchscreen | Panasonic Industrial Automation AWHS1R070 | PASS
X-118 | Hoogendoorn iSii Remote Monitoring | 1 | Hoogendoorn iSii Remote Monitoring | HMS Networks (Ewon) FLEXY20500_00MA | PASS
X-112 | Hydraulic Connectors | 1 | Hydraulic Connectors | commodity — MPN at procurement | PASS
FCV-201–202 | Inlet Flow Control Valve | 2 | Inlet Flow Control Valve · 45 m³/h · DN100 modulating control valve (45 m³/h @ 2 m/s) | — not yet in ledger | PASS
P-103 | Irrigation Pump | 1 | Irrigation Pump · 90 m³/h · 1379x766x1073 mm | Grundfos 96539165 | PASS
I-113 | Leak Detection Sensor | 1 | Leak Detection Sensor | nVent Raychem TT-1000 | PASS
LT-201–213 | Level Transmitter | 13 | Level Transmitter · 0–1.4 m | — not yet in ledger | PASS
X-135 | Leveling Feet | 1 | Leveling Feet | commodity — MPN at procurement | PASS
I-111 | Low Pressure Switch | 1 | Low Pressure Switch | Danfoss 060-121966 | PASS
EP-101 | Main Switchboard | 1 | Main Switchboard · 125 A · 400 V 3-phase LV incomer · 125 A ACB frame (sized to 53 kW connected load, PF 0.9, 25% margin) | Schneider Electric BlokSeT MB301M | PASS
EP-102 | Mains Incomer | 1 | Mains Incomer · 125 A · 400 V 3-phase LV incomer · 125 A ACB frame (sized to 53 kW connected load, PF 0.9, 25% margin) | ABB 1SDA067417R1 | PASS
X-116 / X-122 | Modbus Interface | 2 | Modbus Interface · MERGED ROWS (synonym): 'Modbus Interface' (X-116) + 'Modbus Tcp Interface' (X-122) | — not yet in ledger | PASS
EP-104 | Motor Control Center | 1 | Motor Control Center | Eaton Freedom 2100 | PASS
X-140 | Motor Overload Protection | 1 | Motor Overload Protection | Siemens 3RU2126-4DB0 | PASS
TK-103 | Nutrient Tank | 8 | Nutrient Tank · 1.1 m dia x 1.1 m | bespoke fabrication to drawing — see sizing basis | PASS
I-107 | Orp Sensor | 1 | Orp Sensor | Endress+Hauser CPS12D | PASS
X-138 | Overcurrent Protection | 1 | Overcurrent Protection | Schneider Electric LV430630 | PASS
X-132 | Painted Carbon Steel Skid Frame | 1 | Painted Carbon Steel Skid Frame · 2.3 m dia x 2.4 m | bespoke fabrication to drawing — see sizing basis | PASS
X-133 | Painted Steel Skid Frame | 1 | Painted Steel Skid Frame · 2.3 m dia x 2.4 m | bespoke fabrication to drawing — see sizing basis | PASS
X-106 | Permeate Outlet | 1 | Permeate Outlet | commodity — MPN at procurement | PASS
AT-201 | pH Analyser | 1 | pH Analyser · pH 0–14 (control 0.3) | Hach LXV404.99.05112 | PASS
I-106 | Ph Sensor | 1 | Ph Sensor | Endress+Hauser CPS11E | PASS
X-114 / X-121 | PLC Controller | 2 | PLC Controller · MERGED ROWS (synonym): 'PLC Controller' (X-114) + 'Siemens S7 1200 PLC' (X-121) | — not yet in ledger | PASS
X-125 | Pneumatic Actuated Valves | 200 | Pneumatic Actuated Valves | Bürkert Type 2000 | PASS
V-108 | Pneumatic Control Valve | 1 | Pneumatic Control Valve | Bürkert Type 2301 | PASS
X-128 | Power Supply Unit | 1 | Power Supply Unit | Omron Automation and Safety S8VS-09024BP | PASS
V-109 | Pressure Relief Valve | 1 | Pressure Relief Valve · 4 kW · 600x510x660 mm | Goetze Series 851 | PASS
PT-201–217 | Pressure Transmitter | 17 | Pressure Transmitter · 0–5 bar | — not yet in ledger | PASS
X-123 | Remote Monitoring Gateway | 1 | Remote Monitoring Gateway | HMS Networks (Ewon) FLEXY20500_00MA | PASS
Z-101 | Reverse Osmosis Skid | 1 | Reverse Osmosis Skid · 2.3 m dia x 2.4 m | bespoke fabrication to drawing — see sizing basis | PASS
P-101 | Ro High Pressure Pump | 1 | Ro High Pressure Pump · 4 kW · 600x510x660 mm | Grundfos 96502039 | PASS
X-130 | Sample Valves | 1 | Sample Valves | Swagelok SS-42GS4 | PASS
EP-103 | SCADA / Plant Control System | 1 | SCADA / Plant Control System · 53 kW plant | Hoogendoorn iSii | PASS
I-108 | Silica Analyzer | 1 | Silica Analyzer | Hach 5500sc | PASS
V-106 | Softener Vessel | 2 | Softener Vessel · 1.2 m dia x 1.3 m | Pentair Structural 36X72 COMP 6"TF 6"BF | PASS
X-124 / V-107 | Solenoid Valve | 2 | Solenoid Valve · MERGED ROWS (singular/plural): 'Solenoid Valves' (X-124) + 'Solenoid Valve' (V-107) | — not yet in ledger | PASS
X-134 | Sst304 Skid Frame | 1 | Sst304 Skid Frame · 2.3 m dia x 2.4 m | bespoke fabrication to drawing — see sizing basis | PASS
G-201 | Standby Diesel Generator | 1 | Standby Diesel Generator · 60 kVA · 862x733x948 mm | Pramac GBW60P | PASS
X-129 | Surge Protection Device | 1 | Surge Protection Device | Phoenix Contact 2838199 | PASS
I-110 | Tds Sensor | 1 | Tds Sensor | Myron L 750-II-CS51 | PASS
X-108 / X-111 | Terminal Block | 2 | Terminal Block · MERGED ROWS (singular/plural): 'Terminal Blocks' (X-108) + 'Terminal Block' (X-111) | — not yet in ledger | PASS
F-1 | Toray HFU-2020AN RO Membrane Elements | 1 | Toray HFU-2020AN RO Membrane Elements · 364 m² area | bespoke fabrication to drawing — see sizing basis | PASS
TX-101 | Transformer | 1 | Transformer · 75 kW · 1090x927x1199 mm | TBD (detailed design) | PASS
F-2 | Uf Membrane Bank | 1 | Uf Membrane Bank · 364 m² area | bespoke fabrication to drawing — see sizing basis | PASS
Z-102 | Uf Module Bank | 1 | Uf Module Bank | 0 | PASS
Z-103 | Ultrafiltration Module | 1 | Ultrafiltration Module | 0 | PASS
V-102 | Uv Disinfection | 1 | Uv Disinfection · 4 kW · 600x510x660 mm | WEDECO (Xylem) Spektron 30e | PASS
X-115 | Veolia Ro40 Controller | 1 | Veolia Ro40 Controller | OEM-proprietary (no public MPN) | PASS
X-143 | Zoned distribution — department delivery mains | 214 | Zoned distribution — department delivery mains · DN125 PVC-U · 214 m | DN125 PVC-U pressure pipe + fittings + hangers, 214 m (supply) | PASS

## Glossary
Glossary — abbreviations & symbols |  | ↑ Contents
⬤ TAB QUALITY 10/10 · PASS (target ≥8, live from the Quality & Audit score cell) · glossary contract (every term defined + no orphan terms) — every rendered term carries a definition 59/59; terms actually used somewhere in the workbook 59/59 · score = … · full audit: Quality & Audit tab
Plain-English meaning of every abbreviation used on the schedule, drawing, bill-of-materials and cost tabs. Standard engineering nomenclature (British spelling); the same reference applies to any plant.
Pipe sizes & materials
DN | Diameter Nominal — the nominal bore size of a pipe / valve in millimetres (e.g. DN200 ≈ 200 mm bore). A size label, not the exact internal diameter.
CS | Carbon steel — the default structural / pipe steel where no corrosion or hygiene driver applies.
316L | 316L stainless steel — low-carbon austenitic stainless; the corrosion-resistant grade for process-water, oxidiser and hygienic duties.
304 / 304L | 304 / 304L stainless steel — general-purpose austenitic stainless.
DUPLEX | Duplex stainless steel — high-strength, chloride-corrosion-resistant stainless for seawater / brackish duties.
HDPE / PE100 | High-density polyethylene (PE100 grade) — tough, corrosion-free thermoplastic pipe for water / effluent at low pressure.
FRP / GRP | Fibre-reinforced plastic (glass-reinforced plastic) — moulded composite for tanks and vessels.
PVC / uPVC | Poly(vinyl chloride) pipe grades — low-cost drainage / cold-water pipe.
Instrumentation (ISA tags)
ISA | The instrument-tag convention to ISA-5.1 (International Society of Automation) — the letter code naming what an instrument measures and does.
LT | Level Transmitter — measures liquid level.
TT | Temperature Transmitter — measures temperature.
PT | Pressure Transmitter — measures pressure.
FT | Flow Transmitter — measures flow rate.
AT | Analyser Transmitter — measures a composition variable, e.g. dissolved oxygen, pH or redox.
AT (pH) / AT (ORP) | Analyser variant: pH, or oxidation-reduction (redox) potential.
4–20 mA | The standard analogue field-signal current loop (4 mA = zero, 20 mA = full scale).
PLC / SCADA | Programmable Logic Controller / Supervisory Control And Data Acquisition — the plant control system.
Equipment & package tags
P (tag) | Pump — equipment-tag letter (P-101, P-102 …).
TK (tag) | Tank — bulk liquid storage vessel (TK-101 …).
V (tag) | Vessel — pressure / process vessel, guard bed, filter housing (V-101 …).
D (tag) | Drum / separator — knock-out drum, decanter, three-phase separator (D-101 …). The tag scheme's separator letter.
U (tag) | Utility / package unit — a balance-of-plant utility supplied as one packaged item, e.g. an uninterruptible power supply (U-201 …).
Z (tag) | Packaged skid unit — a vendor skid delivered as one assembly, e.g. a reverse-osmosis or ultrafiltration skid (Z-101 …). Distinct from the HVAC zone identifiers Z-01, Z-02 … (see the HVAC group).
EP (tag) | Electrical panel — switchgear, motor-control-centre or control cabinet (EP-101 …).
X (tag) | General / unclassified equipment block (X-101 …).
C (tag) | Column / tower (C-101 …); on the bill of materials a C-numbered row (C01, C02 …) is a CONNECTION line — an interconnecting pipe or cable run.
I (tag) | Field instrument or in-line device (I-101 …).
Valves & safety
FC | Fail Closed — the valve drives to the CLOSED position on loss of signal, air or power.
PSV / PRV | Pressure Safety / Relief Valve — mechanical over-pressure protection.
XV / SDV | Shutdown / emergency-shutdown Valve — fast on/off safety isolation.
PCV | Pressure / Process Control Valve — a modulating control valve.
HV | Hand Valve — manual isolation.
NRV / CV | Non-Return Valve / Check Valve — prevents reverse flow.
Electrical
MCB | Miniature Circuit Breaker.
UPS | Uninterruptible Power Supply — battery-backed supply for control / instruments.
VSD / VFD | Variable-Speed / Variable-Frequency Drive — controls motor speed.
LV / HV | Low Voltage / High Voltage.
ΔU % | Volt-drop percentage — the voltage lost along a cable run as a fraction of the supply voltage (kept within spec, typically ≤ 5 %).
HVAC
HVAC | Heating, Ventilation & Air-Conditioning.
Battery storage (BESS tags)
CH (tag) | Chiller — the liquid-cooling package rejecting battery and PCS waste heat via a coolant loop (CH-101 …).
PCS (tag) | Power Conversion System — the bidirectional inverter converting between the battery's DC bus and the AC grid connection (PCS-101 …).
SG (tag) | Switchgear — the AC main breaker / protection and isolation assembly at the grid-connection point (SG-101 …).
Bill-of-materials status codes
BESPOKE | Made-to-order item — fabricated / engineered to spec; no off-the-shelf part number.
UTILITY | A utility / commodity item (pipework, cable, civils) priced parametrically.
SYSTEM | A multi-part packaged system priced as one unit.
IDENTIFIED | A specific real product has been matched (manufacturer + part number).
NOT FOUND | No catalogue match yet — the price is an engineering estimate.
INSTRUMENT | A field-instrument line.
Units
m³/h | Cubic metres per hour — volumetric flow.
m³/s | Cubic metres per second — volumetric flow.
kW / kWh | Kilowatt (power) / kilowatt-hour (energy).
mg/L | Milligrams per litre — concentration (e.g. dissolved oxygen).
bar / barg | Pressure / pressure gauge (above atmospheric).
t/yr | Tonnes per year — annual throughput.
Tag-prefix families (self-documented from the bill of materials)
F (tag) | Tag prefix for 'Toray HFU-2020AN RO Membrane Elements' and its numbered siblings (F-101, F-102, …) — self-documented from the bill of materials' own first occurrence.
FCV (tag) | Tag prefix for 'Inlet Flow Control Valve' and its numbered siblings (FCV-101, FCV-102, …) — self-documented from the bill of materials' own first occurrence.
G (tag) | Tag prefix for 'Standby Diesel Generator' and its numbered siblings (G-101, G-102, …) — self-documented from the bill of materials' own first occurrence.
M (tag) | Tag prefix for 'Distribution Manifold' and its numbered siblings (M-101, M-102, …) — self-documented from the bill of materials' own first occurrence.
TX (tag) | Tag prefix for 'Distribution Transformer' and its numbered siblings (TX-101, TX-102, …) — self-documented from the bill of materials' own first occurrence.

## Audit data
Audit data — the embedded operands behind the live verdict formulas |  |  |  |  | ↑ Contents
⬤ TAB QUALITY 10/10 · PASS (target ≥8, live from the Quality & Audit score cell) · audit-operand register contract (every embedded operand carries its label + provenance; per-row Cell check formulas) — cell completeness+type contract 304/304 · score = … · full audit: Quality & Audit tab
Every check in this workbook is a LIVE formula. Where a check compares against data that lives outside the workbook (the single-line drawing, the engineering contract, a build-time classification), the compared value is EMBEDDED here with its provenance — so the workbook contains everything its own verdicts depend on, and the formula bar on any verdict cell shows exactly which operands it judges.
# | Group | Operand | Value | Provenance (where this value comes from) | Cell check
1 | Sense-check | all-in cost — LLM verdict | ok | benchmarkDivergence.findings[].verdict (scripts/lib/benchmark-expectation.ts) | PASS
2 | Sense-check | output — irrigation_flow — LLM verdict | warn | benchmarkDivergence.findings[].verdict (scripts/lib/benchmark-expectation.ts) | PASS
3 | Sense-check | output — ro_permeate_flow — LLM verdict | ok | benchmarkDivergence.findings[].verdict (scripts/lib/benchmark-expectation.ts) | PASS
4 | Sense-check | output — storage_capacity — LLM verdict | ok | benchmarkDivergence.findings[].verdict (scripts/lib/benchmark-expectation.ts) | PASS
5 | Equipment register — drawing-name match | D-101 · 3 Phase Power Input | 5 | parts_ledger.py covered() matcher — 5/7 drawing surface(s) matched this part's name (parts-ledger.json equipment[].coverage, tag D-101) | PASS
6 | Equipment register — drawing-name match | EP-101 · Main Switchboard | 5 | parts_ledger.py covered() matcher — 5/7 drawing surface(s) matched this part's name (parts-ledger.json equipment[].coverage, tag EP-101) | PASS
7 | Equipment register — drawing-name match | EP-102 · Mains Incomer | 3 | parts_ledger.py covered() matcher — 3/7 drawing surface(s) matched this part's name (parts-ledger.json equipment[].coverage, tag EP-102) | PASS
8 | Equipment register — drawing-name match | EP-103 · SCADA / Plant Control System | 7 | parts_ledger.py covered() matcher — 7/7 drawing surface(s) matched this part's name (parts-ledger.json equipment[].coverage, tag EP-103) | PASS
9 | Equipment register — drawing-name match | EP-104 · Motor Control Center | 4 | parts_ledger.py covered() matcher — 4/7 drawing surface(s) matched this part's name (parts-ledger.json equipment[].coverage, tag EP-104) | PASS
10 | Equipment register — drawing-name match | G-201 · Standby Diesel Generator | 4 | parts_ledger.py covered() matcher — 4/7 drawing surface(s) matched this part's name (parts-ledger.json equipment[].coverage, tag G-201) | PASS
11 | Equipment register — drawing-name match | I-102 · Electrical Control Cabinet | 5 | parts_ledger.py covered() matcher — 5/7 drawing surface(s) matched this part's name (parts-ledger.json equipment[].coverage, tag I-102) | PASS
12 | Equipment register — drawing-name match | I-103 · Digital Control Panel | 5 | parts_ledger.py covered() matcher — 5/7 drawing surface(s) matched this part's name (parts-ledger.json equipment[].coverage, tag I-103) | PASS
13 | Equipment register — drawing-name match | M-101 · Distribution Manifold | 5 | parts_ledger.py covered() matcher — 5/7 drawing surface(s) matched this part's name (parts-ledger.json equipment[].coverage, tag M-101) | PASS
14 | Equipment register — drawing-name match | P-101 · Ro High Pressure Pump | 7 | parts_ledger.py covered() matcher — 7/7 drawing surface(s) matched this part's name (parts-ledger.json equipment[].coverage, tag P-101) | PASS
15 | Equipment register — drawing-name match | P-102 · Hand Watering Pump | 7 | parts_ledger.py covered() matcher — 7/7 drawing surface(s) matched this part's name (parts-ledger.json equipment[].coverage, tag P-102) | PASS
16 | Equipment register — drawing-name match | P-103 · Drain Transfer Pump | 6 | parts_ledger.py covered() matcher — 6/7 drawing surface(s) matched this part's name (parts-ledger.json equipment[].coverage, tag P-103) | PASS
17 | Equipment register — drawing-name match | P-104 · Drain Transfer Pump | 7 | parts_ledger.py covered() matcher — 7/7 drawing surface(s) matched this part's name (parts-ledger.json equipment[].coverage, tag P-104) | PASS
18 | Equipment register — drawing-name match | P-105 · Irrigation Pump | 0 | parts_ledger.py covered() matcher — 0/? drawing surface(s) matched this part's name (parts-ledger.json equipment[].coverage, tag P-105) | PASS
19 | Equipment register — drawing-name match | P-106 · Fertigation Dosing Pump | 7 | parts_ledger.py covered() matcher — 7/7 drawing surface(s) matched this part's name (parts-ledger.json equipment[].coverage, tag P-106) | PASS
20 | Equipment register — drawing-name match | P-107 · Fertigation Dosing Pump | 7 | parts_ledger.py covered() matcher — 7/7 drawing surface(s) matched this part's name (parts-ledger.json equipment[].coverage, tag P-107) | PASS
21 | Equipment register — drawing-name match | TK-101 · Cip Tank | 5 | parts_ledger.py covered() matcher — 5/7 drawing surface(s) matched this part's name (parts-ledger.json equipment[].coverage, tag TK-101) | PASS
22 | Equipment register — drawing-name match | TK-102 · Cleaning Tank | 5 | parts_ledger.py covered() matcher — 5/7 drawing surface(s) matched this part's name (parts-ledger.json equipment[].coverage, tag TK-102) | PASS
23 | Equipment register — drawing-name match | TK-103 · Nutrient Tank | 5 | parts_ledger.py covered() matcher — 5/7 drawing surface(s) matched this part's name (parts-ledger.json equipment[].coverage, tag TK-103) | PASS
24 | Equipment register — drawing-name match | TK-104 · Nutrient Tank | 5 | parts_ledger.py covered() matcher — 5/7 drawing surface(s) matched this part's name (parts-ledger.json equipment[].coverage, tag TK-104) | PASS
25 | Equipment register — drawing-name match | TK-105 · Nutrient Tank | 5 | parts_ledger.py covered() matcher — 5/7 drawing surface(s) matched this part's name (parts-ledger.json equipment[].coverage, tag TK-105) | PASS
26 | Equipment register — drawing-name match | TK-106 · Drain Water Tank | 5 | parts_ledger.py covered() matcher — 5/7 drawing surface(s) matched this part's name (parts-ledger.json equipment[].coverage, tag TK-106) | PASS
27 | Equipment register — drawing-name match | TK-107 · Drain Water Tank | 5 | parts_ledger.py covered() matcher — 5/7 drawing surface(s) matched this part's name (parts-ledger.json equipment[].coverage, tag TK-107) | PASS
28 | Equipment register — drawing-name match | TK-108 · Fresh Water Tank | 5 | parts_ledger.py covered() matcher — 5/7 drawing surface(s) matched this part's name (parts-ledger.json equipment[].coverage, tag TK-108) | PASS
29 | Equipment register — drawing-name match | TK-109 · Nutrient Tank | 5 | parts_ledger.py covered() matcher — 5/7 drawing surface(s) matched this part's name (parts-ledger.json equipment[].coverage, tag TK-109) | PASS
30 | Equipment register — drawing-name match | TK-110 · Nutrient Tank | 5 | parts_ledger.py covered() matcher — 5/7 drawing surface(s) matched this part's name (parts-ledger.json equipment[].coverage, tag TK-110) | PASS
31 | Equipment register — drawing-name match | TK-111 · Nutrient Tank | 5 | parts_ledger.py covered() matcher — 5/7 drawing surface(s) matched this part's name (parts-ledger.json equipment[].coverage, tag TK-111) | PASS
32 | Equipment register — drawing-name match | TK-112 · Nutrient Tank | 5 | parts_ledger.py covered() matcher — 5/7 drawing surface(s) matched this part's name (parts-ledger.json equipment[].coverage, tag TK-112) | PASS
33 | Equipment register — drawing-name match | TK-113 · Nutrient Tank | 5 | parts_ledger.py covered() matcher — 5/7 drawing surface(s) matched this part's name (parts-ledger.json equipment[].coverage, tag TK-113) | PASS
34 | Equipment register — drawing-name match | TK-114 · Drain Collection Sump | 5 | parts_ledger.py covered() matcher — 5/7 drawing surface(s) matched this part's name (parts-ledger.json equipment[].coverage, tag TK-114) | PASS
35 | Equipment register — drawing-name match | TK-115 · Drain Collection Sump | 5 | parts_ledger.py covered() matcher — 5/7 drawing surface(s) matched this part's name (parts-ledger.json equipment[].coverage, tag TK-115) | PASS
36 | Equipment register — drawing-name match | TX-101 · Transformer | 3 | parts_ledger.py covered() matcher — 3/7 drawing surface(s) matched this part's name (parts-ledger.json equipment[].coverage, tag TX-101) | PASS
37 | Equipment register — drawing-name match | TX-102 · Distribution Transformer | 3 | parts_ledger.py covered() matcher — 3/7 drawing surface(s) matched this part's name (parts-ledger.json equipment[].coverage, tag TX-102) | PASS
38 | Equipment register — drawing-name match | U-201 · Control + Instrument UPS | 4 | parts_ledger.py covered() matcher — 4/7 drawing surface(s) matched this part's name (parts-ledger.json equipment[].coverage, tag U-201) | PASS
39 | Equipment register — drawing-name match | V-101 · Gac Filter | 6 | parts_ledger.py covered() matcher — 6/7 drawing surface(s) matched this part's name (parts-ledger.json equipment[].coverage, tag V-101) | PASS
40 | Equipment register — drawing-name match | V-102 · Uv Disinfection | 7 | parts_ledger.py covered() matcher — 7/7 drawing surface(s) matched this part's name (parts-ledger.json equipment[].coverage, tag V-102) | PASS
41 | Equipment register — drawing-name match | V-103 · Gac Softener | 5 | parts_ledger.py covered() matcher — 5/7 drawing surface(s) matched this part's name (parts-ledger.json equipment[].coverage, tag V-103) | PASS
42 | Equipment register — drawing-name match | V-104 · Cloth Filter | 7 | parts_ledger.py covered() matcher — 7/7 drawing surface(s) matched this part's name (parts-ledger.json equipment[].coverage, tag V-104) | PASS
43 | Equipment register — drawing-name match | V-105 · Cloth Filter | 7 | parts_ledger.py covered() matcher — 7/7 drawing surface(s) matched this part's name (parts-ledger.json equipment[].coverage, tag V-105) | PASS
44 | Equipment register — drawing-name match | V-106 · Softener Vessel | 5 | parts_ledger.py covered() matcher — 5/7 drawing surface(s) matched this part's name (parts-ledger.json equipment[].coverage, tag V-106) | PASS
45 | Equipment register — drawing-name match | V-107 · Softener Vessel | 5 | parts_ledger.py covered() matcher — 5/7 drawing surface(s) matched this part's name (parts-ledger.json equipment[].coverage, tag V-107) | PASS
46 | Equipment register — drawing-name match | X-102 · Electrical Control Panel | 0 | parts_ledger.py covered() matcher — 0/? drawing surface(s) matched this part's name (parts-ledger.json equipment[].coverage, tag X-102) | PASS
47 | Equipment register — drawing-name match | X-103 · Concentrate Outlet | 0 | parts_ledger.py covered() matcher — 0/? drawing surface(s) matched this part's name (parts-ledger.json equipment[].coverage, tag X-103) | PASS
48 | Equipment register — drawing-name match | X-104 · Permeate Outlet | 5 | parts_ledger.py covered() matcher — 5/7 drawing surface(s) matched this part's name (parts-ledger.json equipment[].coverage, tag X-104) | PASS
49 | Equipment register — drawing-name match | Z-101 · Reverse Osmosis Skid | 5 | parts_ledger.py covered() matcher — 5/7 drawing surface(s) matched this part's name (parts-ledger.json equipment[].coverage, tag Z-101) | PASS
50 | Equipment register — drawing-name match | Z-102 · Uf Module Bank | 5 | parts_ledger.py covered() matcher — 5/7 drawing surface(s) matched this part's name (parts-ledger.json equipment[].coverage, tag Z-102) | PASS
51 | Equipment register — drawing-name match | Z-103 · Ultrafiltration Module | 3 | parts_ledger.py covered() matcher — 3/7 drawing surface(s) matched this part's name (parts-ledger.json equipment[].coverage, tag Z-103) | PASS
52 | Process schedules · reconciliation | Valve count: schedule vs BoM — SCHEDULE | 231 | valve list (incl. '(×N)' / tag-range multiplicities) | PASS
53 | Process schedules · reconciliation | Valve count: schedule vs BoM — BOM | 233 | BoM lines matching /valve/i whose basis is NOT a network-allowance (excludes zone-kit + hand-watering station allowances — per-zone/per-station pipework tie-ins, not schedule-listed line valves) | PASS
54 | Process schedules · reconciliation | Instrument count: schedule vs BoM — SCHEDULE | 55 | instrument index (raw rows, pre-collapse) | PASS
55 | Process schedules · reconciliation | Instrument count: schedule vs BoM — BOM | 52 | BoM lines matching the instrument family whose requirement is NOT a control-system item, an electrical voltage/current sense or protection element (CT/VT-class — panel-schedule items, not process instruments), or a mount/label accessory of an already-counted instrument | PASS
56 | Regulatory · compliance-gate | verdict (engine) | WARN | engine complianceGate.verdict | PASS
57 | Regulatory · compliance-gate | reason | No class-standards registered for "water_treatment". Compliance check skipped — engineer must verify manually before sale. | engine complianceGate.reason | PASS
58 | Electrical | volt-drop limit (%) | 5 | the schedule's published ≤5% volt-drop band (BS 7671 §525 practice) | PASS
59 | Electrical | MAIN DISTRIBUTION BOARD (TP&N) — system voltage (V) | 400 | panel-schedule.md '## MAIN DISTRIBUTION BOARD (TP&N)' System field | PASS
60 | Electrical | MAIN DISTRIBUTION BOARD (TP&N) — pf·η denominator factor | 1.7321 | √3 for a 3-phase board, 1 for DC / single-phase (from the board's own System field) | PASS
61 | Electrical | Main Switchboard — system voltage (V) | 400 | panel-schedule.md '## Main Switchboard' System field | PASS
62 | Electrical | Main Switchboard — pf·η denominator factor | 1.7321 | √3 for a 3-phase board, 1 for DC / single-phase (from the board's own System field) | PASS
63 | Electrical · reconciliation | MAIN DISTRIBUTION BOARD (TP&N) · [board reconciliation] — Σ-current/busbar ratio | 1 | the schedule's own printed reconciliation line | PASS
64 | Electrical · reconciliation | MAIN DISTRIBUTION BOARD (TP&N) · [board reconciliation] — schedule's own verdict | OK | the schedule's printed OK/REVIEW verdict | PASS
65 | Electrical · reconciliation | MAIN DISTRIBUTION BOARD (TP&N) · [board reconciliation] — busbar rating | 100 A | panel-schedule.md board Field/Value table | PASS
66 | Electrical · reconciliation | MAIN DISTRIBUTION BOARD (TP&N) · [board reconciliation] — evidence |  | build-computed reconciliation reasons ('' = clean) | PASS
67 | Electrical · reconciliation | Main Switchboard · [board reconciliation] — Σ-current/busbar ratio | 1 | the schedule's own printed reconciliation line | PASS
68 | Electrical · reconciliation | Main Switchboard · [board reconciliation] — schedule's own verdict | OK | the schedule's printed OK/REVIEW verdict | PASS
69 | Electrical · reconciliation | Main Switchboard · [board reconciliation] — busbar rating | 20 A | panel-schedule.md board Field/Value table | PASS
70 | Electrical · reconciliation | Main Switchboard · [board reconciliation] — evidence |  | build-computed reconciliation reasons ('' = clean) | PASS
71 | Electrical · reconciliation | system voltage (V) — SCHEDULE | 400 | panel-schedule.md system line | PASS
72 | Electrical · reconciliation | voltage tokens — DRAWING | 400 | every 'N V' token on the single-line drawing | PASS
73 | Electrical · reconciliation | schedule boards ABSENT from the single-line drawing | MAIN DISTRIBUTION BOARD (TP&N) | panel-schedule.md board headings not found in the single-line-diagram.svg text (computed at build; '' = every board found) | PASS
74 | Electrical · reconciliation | schedule boards (named) | MAIN DISTRIBUTION BOARD (TP&N), Main Switchboard | panel-schedule.md '## <board>' headings | PASS
75 | Electrical · reconciliation | transformer rating (kVA) — DRAWING | 75 | read from drawings/single-line-diagram.svg (TX label text) | PASS
76 | Electrical · reconciliation | transformer rating (kVA) — CONTRACT | 75 | orchestratorContract.quantities transformer_kva / main_transformer_kva / transformer_rating_kva | PASS